{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["Comm Addresses","Alarm & Failure Bit Sheet","Coil Address Sample","File and Slave Number"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Comm Addresses","index":0,"n_rows":385,"n_cols":8,"rows_kept":385,"cut":false,"hidden":false,"merged":[]}
["ADDRESS TYPE","READ/WRITE","ORIGINAL MODBUS","RELATIVE MODBUS ADDRESS","RELATIVE MICROLOGIX ADDRESS","ADDRESS TAG","DESCRIPTION","DATA"]
["WORD","READ",null,43001,"N110:000","DI/O Low 16bits","DI/O01(b0)~DI/O16(b15)"]
["WORD","READ",null,43002,"N110:001","DI/O High 16bits","DI/O17(b0)~DI/O32(b15)"]
["WORD","READ",40273,43003,"N110:002","ALARM No.  1 to  16","No.  1(b0)~No. 16(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40274,43004,"N110:003","ALARM No. 17 to  32","No. 17(b0)~No. 32(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40275,43005,"N110:004","ALARM No. 33 to  48","No. 33(b0)~No. 48(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40276,43006,"N110:005","ALARM No. 49 to  64","No. 49(b0)~No. 64(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40277,43007,"N110:006","ALARM No. 65 to  80","No. 65(b0)~No. 80(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40278,43008,"N110:007","ALARM No. 80 to  96","No. 81(b0)~No. 96(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40279,43009,"N110:008","ALARM No. 97 to 112","No. 97(b0)~No.112(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40280,43010,"N110:009","ALARM No.113 to 128","No.113(b0)~No.128(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40289,43011,"N110:010","FAILURE No.  1 to  16","No.  1(b0)~No. 16(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40290,43012,"N110:011","FAILURE No. 17 to  32","No. 17(b0)~No. 32(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40291,43013,"N110:012","FAILURE No. 33 to  48","No. 33(b0)~No. 48(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40292,43014,"N110:013","FAILURE No. 49 to  64","No. 49(b0)~No. 64(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40293,43015,"N110:014","FAILURE No. 65 to  80","No. 65(b0)~No. 80(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40294,43016,"N110:015","FAILURE No. 80 to  96","No. 81(b0)~No. 96(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40295,43017,"N110:016","FAILURE No. 97 to 112","No. 97(b0)~No.112(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40296,43018,"N110:017","FAILURE No.113 to 128","No.113(b0)~No.128(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",40321,43019,"N110:018","AI01","Local Suction Pressure","Industrial Unit X 10^n"]
["WORD","READ",40322,43020,"N110:019","AI02","Discharge Pressure","Industrial Unit X 10^n"]
["WORD","READ",40323,43021,"N110:020","AI03","Oil Supply Pressure","Industrial Unit X 10^n"]
["WORD","READ",40324,43022,"N110:021","AI04","After Filter Pressure","Industrial Unit X 10^n"]
["WORD","READ",40325,43023,"N110:022","AI05","Suction Temperature","Industrial Unit X 10^n"]
["WORD","READ",40326,43024,"N110:023","AI06","Discharge Temperature","Industrial Unit X 10^n"]
["WORD","READ",40327,43025,"N110:024","AI07","Oil Supply Temperature","Industrial Unit X 10^n"]
["WORD","READ",40328,43026,"N110:025","AI08","Oil Separator Temperature","Industrial Unit X 10^n"]
["WORD","READ",40329,43027,"N110:026","AI09","Intermediate Pressure","Industrial Unit X 10^n"]
["WORD","READ",40330,43028,"N110:027","AI10","Intermediate Temperature","Industrial Unit X 10^n"]
["WORD","READ",40331,43029,"N110:028","AI11","Chiller Liquid Level","Industrial Unit X 10^n"]
["WORD","READ",40332,43030,"N110:029","AI12","Compressor Motor Electric Current","Industrial Unit X 10^n"]
["WORD","READ",40333,43031,"N110:030","AI13","Chiller Inlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",40334,43032,"N110:031","AI14","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",40335,43033,"N110:032","AI15","Low Stage Slide Valve Position","Industrial Unit X 10^n"]
["WORD","READ",40336,43034,"N110:033","AI16","High Satge Slide Valve position/Vi Port Slide Valve Position","Industrial Unit X 10^n"]
["WORD","READ",40337,43035,"N110:034","AI17","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40338,43036,"N110:035","AI18","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40339,43037,"N110:036","AI19","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40340,43038,"N110:037","AI20","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40341,43039,"N110:038","AI21","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40342,43040,"N110:039","AI22","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40343,43041,"N110:040","AI23","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40344,43042,"N110:041","AI24","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40345,43043,"N110:042","AI25","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40346,43044,"N110:043","AI26","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40347,43045,"N110:044","AI27","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40348,43046,"N110:045","AI28","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40349,43047,"N110:046","AI29","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40350,43048,"N110:047","AI30","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40351,43049,"N110:048","AI31","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40352,43050,"N110:049","AI32","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40385,43051,"N110:050","AI65","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40386,43052,"N110:051","AI66","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40387,43053,"N110:052","AI67","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40388,43054,"N110:053","AI68","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40389,43055,"N110:054","AI69","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40390,43056,"N110:055","AI70","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40391,43057,"N110:056","AI71","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40392,43058,"N110:057","AI72","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40393,43059,"N110:058","AI73","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40394,43060,"N110:059","AI74","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40395,43061,"N110:060","AI75","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40396,43062,"N110:061","AI76","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40397,43063,"N110:062","AI77","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40398,43064,"N110:063","AI78","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40399,43065,"N110:064","AI79","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",40400,43066,"N110:065","AI80","Pseudo Analog Input","Industrial Unit X 10^n"]
["WORD","READ",null,43067,"N110:066","PID 1/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43068,"N110:067","PID 1/16PV","Local/System Suction/Discharge Pressure","Industrial Unit X 10^n"]
["WORD","READ",null,43069,"N110:068","PID 1/16MV","Output of Low Stage Slide Valve Control on Pressure/Combined","0.0~100.0%:0~1000"]
["WORD","READ",null,43070,"N110:069","PID 2/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43071,"N110:070","PID 2/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",null,43072,"N110:071","PID 2/16MV","Output of Low Stage Slide Valve Control on Temperature","0.0~100.0%:0~1000"]
["WORD","READ",null,43073,"N110:072","PID 3/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43074,"N110:073","PID 3/16PV","Suction Superheat","Industrial Unit X 10^n"]
["WORD","READ",null,43075,"N110:074","PID 3/16MV","Output of Chiller Expansion Vale Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43076,"N110:075","PID 4/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43077,"N110:076","PID 4/16PV","Local Suction Pressure","Industrial Unit X 10^n"]
["WORD","READ",null,43078,"N110:077","PID 4/16MV","Output of Limitation of Cheller Expansion Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43079,"N110:078","PID 5/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43080,"N110:079","PID 5/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",null,43081,"N110:080","PID 5/16MV","Output of Limitation of Cheller Expansion Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43082,"N110:081","PID 6/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43083,"N110:082","PID 6/16PV","Intermediate Superheat","Industrial Unit X 10^n"]
["WORD","READ",null,43084,"N110:083","PID 6/16MV","Output of Economizer/Inter Cooler Expansion Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43085,"N110:084","PID 7/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43086,"N110:085","PID 7/16PV","Discharge Temperature/Superheat","Industrial Unit X 10^n"]
["WORD","READ",null,43087,"N110:086","PID 7/16MV","Output of Liquid Injection Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43088,"N110:087","PID 8/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43089,"N110:088","PID 8/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",null,43090,"N110:089","PID 8/16MV","Output of Brine Flow Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43091,"N110:090","PID 9/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43092,"N110:091","PID 9/16PV","Local/System Discharge pressure","Industrial Unit X 10^n"]
["WORD","READ",null,43093,"N110:092","PID 9/16MV","Output of Condenser Fan/Pump Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43094,"N110:093","PID10/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43095,"N110:094","PID10/16PV","Intermediate Pressure","Industrial Unit X 10^n"]
["WORD","READ",null,43096,"N110:095","PID10/16MV","Output of High Stage Slide Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43097,"N110:096","PID11/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43098,"N110:097","PID11/16PV","Local/System Suction/Discharge Pressure","Industrial Unit X 10^n"]
["WORD","READ",null,43099,"N110:098","PID11/16MV","Output of Compressor Motor on Pressure/Combined","0.0~100.0%:0~1000"]
["WORD","READ",null,43100,"N110:099","PID12/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43101,"N110:100","PID12/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",null,43102,"N110:101","PID12/16MV","Output of Compressor Motor on Temperature","0.0~100.0%:0~1000"]
["WORD","READ",null,43103,"N110:102","PID13/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43104,"N110:103","PID13/16PV","Suction Superheat2","Industrial Unit X 10^n"]
["WORD","READ",null,43105,"N110:104","PID13/16MV","Output of Chiller Expansion Vale2 Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43106,"N110:105","PID14/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43107,"N110:106","PID14/16PV","Suction Pressure2","Industrial Unit X 10^n"]
["WORD","READ",null,43108,"N110:107","PID14/16MV","Output of Limitation of Cheller Expansion Valve2 Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43109,"N110:108","PID15/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",null,43110,"N110:109","PID15/16PV","Chiller Liquid Level","Industrial Unit X 10^n"]
["WORD","READ",null,43111,"N110:110","PID15/16MV","Output of Chiller Liquid Level Control","0.0~100.0%:0~1000"]
["WORD","READ",null,43112,"N110:111","PID16/16SV","Undefined","Industrial Unit X 10^n"]
["WORD","READ",null,43113,"N110:112","PID16/16PV","Undefined","Industrial Unit X 10^n"]
["WORD","READ",null,43114,"N110:113","PID16/16MV","Undefined","0.0~100.0%:0~1000"]
["WORD","READ",null,43115,"N110:114","RUN TIME Low","Low 16bits of 32bits Hours"]
["WORD","READ",null,43116,"N110:115","RUN TIME High","High 16bits of 32bits Hours","RUN TIME = (R43065) + 65536 X (R43066)"]
["WORD","READ",null,43117,"N110:116","TOTAL RUN TIME Low","Low 16bits of 32bits Hours"]
["WORD","READ",null,43118,"N110:117","TOTAL RUN TIME High","High 16bits of 32bits Hours","RUN TIME = (R43067) + 65536 X (R43068)"]
["WORD","READ",null,43119,"N110:118","RTC","Week","0(SUN.) to Six(SAT.)"]
["WORD","READ",null,43120,"N110:119","RTC","Month","1 to 12"]
["WORD","READ",null,43121,"N110:120","RTC","Day","1 to 31"]
["WORD","READ",null,43122,"N110:121","RTC","Year","A.D. Four digits."]
["WORD","READ",null,43123,"N110:122","RTC","Hour","0 to 23"]
["WORD","READ",null,43124,"N110:123","RTC","Minute","0 to 59"]
["WORD","READ",null,43125,"N110:124","RTC","Second","0 to 59"]
["WORD","READ",null,43126,"N110:125","Undefined"]
["WORD","READ",null,43127,"N110:126","Undefined"]
["WORD","READ",null,43128,"N110:127","Undefined"]
["WORD","READ/WRITE",null,43129,"N110:128","CUT IN Set Point","Pressure or Temperature","Industrial Unit X 10^n"]
["WORD","READ/WRITE",null,43130,"N110:129","CUT OUT Set Point","Pressure or Temperature"]
["WORD","READ/WRITE",null,43131,"N110:130","Pressure Set Point of CAPACITY CONTROL"]
["WORD","READ/WRITE",null,43132,"N110:131","Temperature Set Point of CAPACITY CONTROL"]
["WORD","READ/WRITE",null,43133,"N110:132","Capacity Set Point",null,"0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43134,"N110:133","Undefined"]
["WORD","READ/WRITE",null,43135,"N110:134","Undefined"]
["WORD","READ/WRITE",null,43136,"N110:135","Undefined"]
["WORD","READ/WRITE",null,43137,"N110:136","Undefined"]
["WORD","READ/WRITE",null,43138,"N110:137","Undefined"]
["WORD","READ/WRITE",null,43139,"N110:138","Undefined"]
["WORD","READ/WRITE",null,43140,"N110:139","Undefined"]
["WORD","READ/WRITE",null,43141,"N110:140","Undefined"]
["WORD","READ/WRITE",null,43142,"N110:141","Undefined"]
["WORD","READ/WRITE",null,43143,"N110:142","Undefined"]
["WORD","READ/WRITE",null,43144,"N110:143","Undefined"]
["WORD","READ/WRITE",null,43145,"N110:144","PID 1/16MVL","Set Point MVL of CAPACITY CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43146,"N110:145","PID 1/16MVH","Set Point MVH of CAPACITY CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43147,"N110:146","PID 2/16MVL","Set Point MVL of CAPACITY CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43148,"N110:147","PID 2/16MVH","Set Point MVH of CAPACITY CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43149,"N110:148","PID11/16MVL","Set Point MVL of VFD COMPRESSOR CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43150,"N110:149","PID11/16MVH","Set Point MVH of VFD COMPRESSOR CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43151,"N110:150","PID12/16MVL","Set Point MVL of VFD COMPRESSOR CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43152,"N110:151","PID12/16MVH","Set Point MVH of VFD COMPRESSOR CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",null,43153,"N110:152","MODE SELECT","OPERATION MODE>OPERATION","(0):LOCAL\n,1:REMOTE\n,2:COMM\n,3:AUTO STAGE\n,4:Not Use\n,5:AUTO STAGE REMOTE\n,6:AUTO STAGE COMM"]
["WORD","READ/WRITE",null,43154,"N110:153","AUTO START SELECT","OPERATION MODE>COMPRESSOR AUTO START/STOP ","0:NO,(1):YES"]
["WORD","READ/WRITE",null,43155,"N110:154","SET POINT No. SELSECT","SET POINTS>SCHEDULER>CUT IN/CUT OUT","(0):SETPOINT #1\n,1:SETPOINT #2\n,2:SETPOINT #3\n,3:SETPOINT #4\n,4:SCHEDULER\n,5:COMM"]
["WORD","READ/WRITE",null,43156,"N110:155","SET POINT No. SELSECT","SET POINTS>SCHEDULER>CONTROL TARGET","(0):SETPOINT #1\n,1:SETPOINT #2\n,2:SETPOINT #3\n,3:SETPOINT #4\n,4:SCHEDULER\n,5:COMM"]
["WORD","READ/WRITE",null,43157,"N110:156","ALARM/FAILURE SELSCT","OPERATION MODE>ALARM/FAILURE","(0):SET POINT#1,1:SET POINT#2"]
["WORD","READ/WRITE",null,43158,"N110:157","CAPACITY CONTROL SELSECT","CAPACITY CONTROL>MONITOR>OPERATION","(0):MANUAL\n,1:AUTO\n,2:REMOTE DIGITAL\n,3:REMOTE ANALOG\n,4:COMM"]
["WORD","READ/WRITE",null,43159,"N110:158","VFD COMPRESSOR CONTROL SELECT","VFD COMPRESSOR CONTROL>MONITOR>OPERATION","(0):MANUAL\n,1:AUTO\n,2:REMOTE DIGITAL\n,3:REMOTE ANALOG\n,4:COMM"]
["WORD","READ/WRITE",null,43160,"N110:159",null,"CAPACITY CONTROL>MVL%/MVH% BY COMM","(0):DISABLE,1:ENABLE"]
["WORD","READ/WRITE",null,43161,"N110:160","Undefined"]
["WORD","READ/WRITE",null,43162,"N110:161","Undefined"]
["WORD","READ/WRITE",null,43163,"N110:162","Undefined"]
["WORD","READ/WRITE",null,43164,"N110:163","Undefined"]
["WORD","READ/WRITE",null,43165,"N110:164","Undefined"]
["WORD","READ/WRITE",null,43166,"N110:165","Undefined"]
["WORD","READ/WRITE",null,43167,"N110:166","Undefined"]
["WORD","READ/WRITE",null,43168,"N110:167","Undefined"]
["WORD","READ/WRITE",null,43169,"N110:168","Undefined"]
["WORD","READ/WRITE",null,43170,"N110:169","Undefined"]
["WORD","READ/WRITE",null,43171,"N110:170","Undefined"]
["WORD","READ/WRITE",null,43172,"N110:171","Undefined"]
["WORD","READ/WRITE",null,43173,"N110:172","Undefined"]
["WORD","READ/WRITE",null,43174,"N110:173","Undefined"]
["WORD","READ/WRITE",null,43175,"N110:174","Undefined"]
["WORD","READ/WRITE",null,43176,"N110:175","Undefined"]
["WORD","READ/WRITE",null,43177,"N110:176","Undefined"]
["WORD","READ/WRITE",null,43178,"N110:177","Undefined"]
["WORD","READ/WRITE",null,43179,"N110:178","Undefined"]
["WORD","READ/WRITE",null,43180,"N110:179","Undefined"]
["WORD","READ/WRITE",null,43181,"N110:180","Undefined"]
["WORD","READ/WRITE",null,43182,"N110:181","Undefined"]
["WORD","READ/WRITE",null,43183,"N110:182","Undefined"]
["WORD","READ/WRITE",null,43184,"N110:183","Undefined"]
["WORD","READ/WRITE",null,43185,"N110:184","Undefined"]
["WORD","READ/WRITE",null,43186,"N110:185","Undefined"]
["WORD","READ/WRITE",null,43187,"N110:186","Undefined"]
["WORD","READ/WRITE",null,43188,"N110:187","Undefined"]
["WORD","READ/WRITE",null,43189,"N110:188","Undefined"]
["WORD","READ/WRITE",null,43190,"N110:189","Undefined"]
["WORD","READ/WRITE",null,43191,"N110:190","Undefined"]
["WORD","READ/WRITE",null,43192,"N110:191","Undefined"]
["WORD","READ/WRITE",null,43193,"N110:192","Reserved"]
["WORD","READ/WRITE",null,43194,"N110:193","Reserved"]
["WORD","READ/WRITE",null,43195,"N110:194","Reserved"]
["WORD","READ/WRITE",null,43196,"N110:195","Reserved"]
["WORD","READ/WRITE",null,43197,"N110:196","Reserved"]
["WORD","READ/WRITE",null,43198,"N110:197","Reserved"]
["WORD","READ/WRITE",null,43199,"N110:198","Reserved"]
["WORD","READ/WRITE",null,43200,"N110:199","Reserved"]
["WORD","READ/WRITE",null,43201,"N110:200","Reserved"]
["WORD","READ/WRITE",null,43202,"N110:201","Reserved"]
["WORD","READ/WRITE",null,43203,"N110:202","Reserved"]
["WORD","READ/WRITE",null,43204,"N110:203","Reserved"]
["WORD","READ/WRITE",null,43205,"N110:204","Reserved"]
["WORD","READ/WRITE",null,43206,"N110:205","Reserved"]
["WORD","READ/WRITE",null,43207,"N110:206","Reserved"]
["WORD","READ/WRITE",null,43208,"N110:207","Reserved"]
["WORD","READ/WRITE",null,43209,"N110:208","Reserved"]
["WORD","READ/WRITE",null,43210,"N110:209","Reserved"]
["WORD","READ/WRITE",null,43211,"N110:210","Reserved"]
["WORD","READ/WRITE",null,43212,"N110:211","Reserved"]
["WORD","READ/WRITE",null,43213,"N110:212","Reserved"]
["WORD","READ/WRITE",null,43214,"N110:213","Reserved"]
["WORD","READ/WRITE",null,43215,"N110:214","Reserved"]
["WORD","READ/WRITE",null,43216,"N110:215","Reserved"]
["WORD","READ/WRITE",null,43217,"N110:216","Reserved"]
["WORD","READ/WRITE",null,43218,"N110:217","Reserved"]
["WORD","READ/WRITE",null,43219,"N110:218","Reserved"]
["WORD","READ/WRITE",null,43220,"N110:219","Reserved"]
["WORD","READ/WRITE",null,43221,"N110:220","Reserved"]
["WORD","READ/WRITE",null,43222,"N110:221","Reserved"]
["WORD","READ/WRITE",null,43223,"N110:222","Reserved"]
["WORD","READ/WRITE",null,43224,"N110:223","Reserved"]
["WORD","READ/WRITE",null,43225,"N110:224","Reserved"]
["WORD","READ/WRITE",null,43226,"N110:225","Reserved"]
["WORD","READ/WRITE",null,43227,"N110:226","Reserved"]
["WORD","READ/WRITE",null,43228,"N110:227","Reserved"]
["WORD","READ/WRITE",null,43229,"N110:228","Reserved"]
["WORD","READ/WRITE",null,43230,"N110:229","Reserved"]
["WORD","READ/WRITE",null,43231,"N110:230","Reserved"]
["WORD","READ/WRITE",null,43232,"N110:231","Reserved"]
["WORD","READ/WRITE",null,43233,"N110:232","Reserved"]
["WORD","READ/WRITE",null,43234,"N110:233","Reserved"]
["WORD","READ/WRITE",null,43235,"N110:234","Reserved"]
["WORD","READ/WRITE",null,43236,"N110:235","Reserved"]
["WORD","READ/WRITE",null,43237,"N110:236","Reserved"]
["WORD","READ/WRITE",null,43238,"N110:237","Reserved"]
["WORD","READ/WRITE",null,43239,"N110:238","Reserved"]
["WORD","READ/WRITE",null,43240,"N110:239","Reserved"]
["WORD","READ/WRITE",null,43241,"N110:240","Reserved"]
["WORD","READ/WRITE",null,43242,"N110:241","Reserved"]
["WORD","READ/WRITE",null,43243,"N110:242","Reserved"]
["WORD","READ/WRITE",null,43244,"N110:243","Reserved"]
["WORD","READ/WRITE",null,43245,"N110:244","Reserved"]
["WORD","READ/WRITE",null,43246,"N110:245","Reserved"]
["WORD","READ/WRITE",null,43247,"N110:246","Reserved"]
["WORD","READ/WRITE",null,43248,"N110:247","Reserved"]
["WORD","READ/WRITE",null,43249,"N110:248","Reserved"]
["WORD","READ/WRITE",null,43250,"N110:249","Reserved"]
["WORD","READ/WRITE",null,43251,"N111:000","Reserved"]
["WORD","READ/WRITE",null,43252,"N111:001","Reserved"]
["WORD","READ/WRITE",null,43253,"N111:002","Reserved"]
["WORD","READ/WRITE",null,43254,"N111:003","Reserved"]
["WORD","READ/WRITE",null,43255,"N111:004","Reserved"]
["WORD","READ/WRITE",null,43256,"N111:005","Reserved"]
["WORD","READ",null,43257,"N111:006","STATUS","CURRENT CUT-IN SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",null,43258,"N111:007","STATUS","CURRENT PRESSURE CONTROL SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",null,43259,"N111:008","STATUS","CURRENT TEMPERATURE CONTROL SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",null,43260,"N111:009","STATUS","CURRENT CUT-OUT SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",null,43261,"N111:010","STATUS","ALARM STATUS","(0) NO ALARM - NO FAILURE, 1: ALARM - NO FAILURE, 2: NO ALARM -FAILURE, 3: ALARM - FAILURE"]
["WORD","READ",null,43262,"N111:011","STATUS","COMPRESSOR OPERATION MODE","(0) LOCAL-OFF, 1: LOCAL-ON, 2: REMOTE-OFF, 3: REMOTE-ON, 4: COMM-OFF, 5: COMM-ON, 6:AUTO STAGE-OFF, 7:AUTO STAGE-ON"]
["WORD","READ",null,43263,"N111:012","STATUS","COMPRESSOR STATUS","(0) STOP, 1: ANTI CYCLE, 2: AUTO STOP, 3: CUT IN, 4: SYSTEM START, 5: OIL PUMP START, 6: PRE START, 7: START, 8: RUN, 9: CUT OUT, 10: PUMP OUT"]
["WORD","READ",null,43264,"N111:013","STATUS","DELAY TIMERS TO TIME UP","SECONDS"]
["WORD","READ",null,43265,"N111:014","STATUS","VFD COMPRESSOR REVOLUTION (MOTOR SPEED)","RPM/HZ"]
["WORD","READ",null,43266,"N111:015","STATUS","VFD CONDENSER REVOLUTION","RPM/HZ"]
["WORD","READ",null,43267,"N111:016","Reserved","Reserved"]
["WORD","READ",null,43268,"N111:017","Reserved","Reserved"]
["WORD","READ",null,43269,"N111:018","Reserved","Reserved"]
["WORD","READ",null,43270,"N111:019","Reserved","Reserved"]
["WORD","READ",null,43271,"N111:020","Reserved","Reserved"]
["WORD","READ",null,43272,"N111:021","Reserved","Reserved"]
["WORD","READ",null,43273,"N111:022","Reserved","Reserved"]
["WORD","READ",null,43274,"N111:023","Reserved","Reserved"]
["WORD","READ",null,43275,"N111:024","Reserved","Reserved"]
["WORD","READ",null,43276,"N111:025","Reserved","Reserved"]
["WORD","READ",null,43277,"N111:026","Reserved","Reserved"]
["WORD","READ",null,43278,"N111:027","Reserved","Reserved"]
["WORD","READ",null,43279,"N111:028","Reserved","Reserved"]
["WORD","READ",null,43280,"N111:029","Reserved","Reserved"]
["WORD","READ",null,43281,"N111:030","Reserved","Reserved"]
["WORD","READ",null,43282,"N111:031","Reserved","Reserved"]
["WORD","READ",null,43283,"N111:032","Reserved","Reserved"]
["WORD","READ",null,43284,"N111:033","Reserved","Reserved"]
["WORD","READ",null,43285,"N111:034","Reserved","Reserved"]
["WORD","READ",null,43286,"N111:035","Reserved","Reserved"]
["WORD","READ",null,43287,"N111:036","Reserved","Reserved"]
["WORD","READ",null,43288,"N111:037","Reserved","Reserved"]
["WORD","READ",null,43289,"N111:038","Reserved","Reserved"]
["WORD","READ",null,43290,"N111:039","Reserved","Reserved"]
["WORD","READ",null,43291,"N111:040","Reserved","Reserved"]
["WORD","READ",null,43292,"N111:041","Reserved","Reserved"]
["WORD","READ",null,43293,"N111:042","Reserved","Reserved"]
["WORD","READ",null,43294,"N111:043","Reserved","Reserved"]
["WORD","READ",null,43295,"N111:044","Reserved","Reserved"]
["WORD","READ",null,43296,"N111:045","Reserved","Reserved"]
["WORD","READ",null,43297,"N111:046","Reserved","Reserved"]
["WORD","READ",null,43298,"N111:047","Reserved","Reserved"]
["WORD","READ",null,43299,"N111:048","Reserved","Reserved"]
["WORD","READ",null,43300,"N111:049","Reserved","Reserved"]
["WORD","READ",null,43301,"N111:050","Reserved","Reserved"]
["WORD","READ",null,43302,"N111:051","Reserved","Reserved"]
["WORD","READ",null,43303,"N111:052","Reserved","Reserved"]
["WORD","READ",null,43304,"N111:053","Reserved","Reserved"]
["WORD","READ",null,43305,"N111:054","Reserved","Reserved"]
["WORD","READ",null,43306,"N111:055","Reserved","Reserved"]
["WORD","READ",null,43307,"N111:056","Reserved","Reserved"]
["WORD","READ",null,43308,"N111:057","Reserved","Reserved"]
["WORD","READ",null,43309,"N111:058","Reserved","Reserved"]
["WORD","READ",null,43310,"N111:059","Reserved","Reserved"]
["WORD","READ",null,43311,"N111:060","Reserved","Reserved"]
["WORD","READ",null,43312,"N111:061","Reserved","Reserved"]
["WORD","READ",null,43313,"N111:062","Reserved","Reserved"]
["WORD","READ",null,43314,"N111:063","Reserved","Reserved"]
["WORD","READ",null,43315,"N111:064","Reserved","Reserved"]
["WORD","READ",null,43316,"N111:065","Reserved","Reserved"]
["WORD","READ",null,43317,"N111:066","Reserved","Reserved"]
["WORD","READ",null,43318,"N111:067","Reserved","Reserved"]
["WORD","READ",null,43319,"N111:068","Reserved","Reserved"]
["WORD","READ",null,43320,"N111:069","Reserved","Reserved"]
["WORD","READ",null,43321,"N111:070","Reserved","Reserved"]
["WORD","READ",null,43322,"N111:071","Reserved","Reserved"]
["WORD","READ",null,43323,"N111:072","Reserved","Reserved"]
["WORD","READ",null,43324,"N111:073","Reserved","Reserved"]
["WORD","READ",null,43325,"N111:074","Reserved","Reserved"]
["WORD","READ",null,43326,"N111:075","Reserved","Reserved"]
["WORD","READ",null,43327,"N111:076","Reserved","Reserved"]
["WORD","READ",null,43328,"N111:077","Reserved","Reserved"]
["WORD","READ",null,43329,"N111:078","Reserved","Reserved"]
["WORD","READ",null,43330,"N111:079","Reserved","Reserved"]
["WORD","READ",null,43331,"N111:080","Reserved","Reserved"]
["WORD","READ",null,43332,"N111:081","Reserved","Reserved"]
["WORD","READ",null,43333,"N111:082","Reserved","Reserved"]
["WORD","READ",null,43334,"N111:083","Reserved","Reserved"]
["WORD","READ",null,43335,"N111:084","Reserved","Reserved"]
["WORD","READ",null,43336,"N111:085","Reserved","Reserved"]
["WORD","READ",null,43337,"N111:086","Reserved","Reserved"]
["WORD","READ",null,43338,"N111:087","Reserved","Reserved"]
["WORD","READ",null,43339,"N111:088","Reserved","Reserved"]
["WORD","READ",null,43340,"N111:089","Reserved","Reserved"]
["WORD","READ",null,43341,"N111:090","Reserved","Reserved"]
["WORD","READ",null,43342,"N111:091","Reserved","Reserved"]
["WORD","READ",null,43343,"N111:092","Reserved","Reserved"]
["WORD","READ",null,43344,"N111:093","Reserved","Reserved"]
["WORD","READ",null,43345,"N111:094","Reserved","Reserved"]
["WORD","READ",null,43346,"N111:095","Reserved","Reserved"]
["WORD","READ",null,43347,"N111:096","Reserved","Reserved"]
["WORD","READ",null,43348,"N111:097","Reserved","Reserved"]
["WORD","READ",null,43349,"N111:098","Reserved","Reserved"]
["WORD","READ",null,43350,"N111:099","Reserved","Reserved"]
["WORD","READ",null,43351,"N111:100","Reserved","Reserved"]
["WORD","READ",null,43352,"N111:101","Reserved","Reserved"]
["WORD","READ",null,43353,"N111:102","Reserved","Reserved"]
["WORD","READ",null,43354,"N111:103","Reserved","Reserved"]
["WORD","READ",null,43355,"N111:104","Reserved","Reserved"]
["WORD","READ",null,43356,"N111:105","Reserved","Reserved"]
["WORD","READ",null,43357,"N111:106","Reserved","Reserved"]
["WORD","READ",null,43358,"N111:107","Reserved","Reserved"]
["WORD","READ",null,43359,"N111:108","Reserved","Reserved"]
["WORD","READ",null,43360,"N111:109","Reserved","Reserved"]
["WORD","READ",null,43361,"N111:110","Reserved","Reserved"]
["WORD","READ",null,43362,"N111:111","Reserved","Reserved"]
["WORD","READ",null,43363,"N111:112","Reserved","Reserved"]
["WORD","READ",null,43364,"N111:113","Reserved","Reserved"]
["WORD","READ",null,43365,"N111:114","Reserved","Reserved"]
["WORD","READ",null,43366,"N111:115","Reserved","Reserved"]
["WORD","READ",null,43367,"N111:116","Reserved","Reserved"]
["WORD","READ",null,43368,"N111:117","Reserved","Reserved"]
["WORD","READ",null,43369,"N111:118","Reserved","Reserved"]
["WORD","READ",null,43370,"N111:119","Reserved","Reserved"]
["WORD","READ",null,43371,"N111:120","Reserved","Reserved"]
["WORD","READ",null,43372,"N111:121","Reserved","Reserved"]
["WORD","READ",null,43373,"N111:122","Reserved","Reserved"]
["WORD","READ",null,43374,"N111:123","Reserved","Reserved"]
["WORD","READ",null,43375,"N111:124","Reserved","Reserved"]
["WORD","READ",null,43376,"N111:125","Reserved","Reserved"]
["WORD","READ",null,43377,"N111:126","Reserved","Reserved"]
["WORD","READ",null,43378,"N111:127","Reserved","Reserved"]
["WORD","READ",null,43379,"N111:128","Reserved","Reserved"]
["WORD","READ",null,43380,"N111:129","Reserved","Reserved"]
["WORD","READ",null,43381,"N111:130","Reserved","Reserved"]
["WORD","READ",null,43382,"N111:131","Reserved","Reserved"]
["WORD","READ",null,43383,"N111:132","Reserved","Reserved"]
["WORD","READ",null,43384,"N111:133","Reserved","Reserved"]

{"sheet":"Alarm & Failure Bit Sheet","index":1,"n_rows":137,"n_cols":5,"rows_kept":137,"cut":false,"hidden":false,"merged":[[0,0,0,2],[1,0,16,0],[1,1,16,1],[1,2,16,2],[1,4,16,4],[49,0,64,0],[49,1,64,1],[49,2,64,2],[49,4,64,4],[17,0,32,0],[17,1,32,1],[17,2,32,2],[17,4,32,4],[33,0,48,0],[33,1,48,1],[33,2,48,2],[33,4,48,4]]}
["Holding Register",null,null,"Bit Alignment","Reference"]
["Read Only",43003,"ALARM No.  1 to  16","Bit 0:Undefined",40281]
[null,null,null,"Bit 1:⊿OP LOW"]
[null,null,null,"Bit 2:⊿P LOW"]
[null,null,null,"Bit 3:DISCHARGE PRESSURE HIGH"]
[null,null,null,"Bit 4:DISCHARGE TEMPERATURE HIGH"]
[null,null,null,"Bit 5:OIL SUPPLY TEMPERATURE HIGH"]
[null,null,null,"Bit 6:COMPRESSOR MOTOR CURRENT HIGH"]
[null,null,null,"Bit 7:INTERMEDIATE PRESSURE HIGH"]
[null,null,null,"Bit 8:SUCTION PRESSURE LOW"]
[null,null,null,"Bit 9:LEAVING BRINE TEMPERATURE LOW"]
[null,null,null,"Bit10:CAPACITY NO DOWN"]
[null,null,null,"Bit11:SUCTION SUPERHEAT LOW"]
[null,null,null,"Bit12:OIL FILTER"]
[null,null,null,"Bit13:RE-START"]
[null,null,null,"Bit14:HIGH STAGE"]
[null,null,null,"Bit15:INTERMEDIATE SUPERHEAT LOW"]
["Read Only",43004,"ALARM No. 17 to  32","Bit 0:ENTERING BRINE TEMPERATURE LOW",40282]
[null,null,null,"Bit 1:SEPARATOR OIL TEMPERATURE LOW"]
[null,null,null,"Bit 2:⊿OP2 LOW"]
[null,null,null,"Bit 3:SUCTION SUPERHEAT2 LOW"]
[null,null,null,"Bit 4:AUTO Vi SLIDE"]
[null,null,null,"Bit 5:FINE FILTER"]
[null,null,null,"Bit 6:DISCHARGE SUPERHEAT LOW"]
[null,null,null,"Bit 7:SUCTION PRESSURE HIGH"]
[null,null,null,"Bit 8:SUCTION TEMPERATURE HIGH"]
[null,null,null,"Bit 9:CHILLER LIQUID LEVEL LOW"]
[null,null,null,"Bit10:Undefined"]
[null,null,null,"Bit11:Undefined"]
[null,null,null,"Bit12:Undefined"]
[null,null,null,"Bit13:Undefined"]
[null,null,null,"Bit14:Undefined"]
[null,null,null,"Bit15:Undefined"]
["Read Only",43005,"ALARM No. 33 to 48","Bit 0:AUTO STAGE NO REQUEST",40283]
[null,null,null,"Bit 1:AUTO STAGE LIST1 NO RESPONSE"]
[null,null,null,"Bit 2:AUTO STAGE LIST2 NO RESPONSE"]
[null,null,null,"Bit 3:AUTO STAGE LIST3 NO RESPONSE"]
[null,null,null,"Bit 4:AUTO STAGE LIST4 NO RESPONSE"]
[null,null,null,"Bit 5:AUTO STAGE LIST5 NO RESPONSE"]
[null,null,null,"Bit 6:AUTO STAGE LIST6 NO RESPONSE"]
[null,null,null,"Bit 7:AUTO STAGE LIST7 NO RESPONSE"]
[null,null,null,"Bit 8:AUTO STAGE LIST8 NO RESPONSE"]
[null,null,null,"Bit 9:OPTION ANALOG INPUT1 LOW"]
[null,null,null,"Bit10:OPTION ANALOG INPUT1 HIGH"]
[null,null,null,"Bit11:OPTION ANALOG INPUT2 LOW"]
[null,null,null,"Bit12:OPTION ANALOG INPUT2 HIGH"]
[null,null,null,"Bit13:OPTION ANALOG INPUT3 LOW"]
[null,null,null,"Bit14:OPTION ANALOG INPUT3 HIGH"]
[null,null,null,"Bit15:OPTION ANALOG INPUT4 LOW"]
["Read Only",43006,"ALARM No. 49 to  64","Bit 0:OPTION ANALOG INPUT4 HIGH",40284]
[null,null,null,"Bit 1:Undefined (Always OFF.)"]
[null,null,null,"Bit 2:Undefined (Always OFF.)"]
[null,null,null,"Bit 3:Undefined (Always OFF.)"]
[null,null,null,"Bit 4:Undefined (Always OFF.)"]
[null,null,null,"Bit 5:Undefined (Always OFF.)"]
[null,null,null,"Bit 6:Undefined (Always OFF.)"]
[null,null,null,"Bit 7:Undefined (Always OFF.)"]
[null,null,null,"Bit 8:Undefined (Always OFF.)"]
[null,null,null,"Bit 9:Undefined (Always OFF.)"]
[null,null,null,"Bit10:Undefined (Always OFF.)"]
[null,null,null,"Bit11:Undefined (Always OFF.)"]
[null,null,null,"Bit12:Undefined (Always OFF.)"]
[null,null,null,"Bit13:Undefined (Always OFF.)"]
[null,null,null,"Bit14:Undefined (Always OFF.)"]
[null,null,null,"Bit15:Undefined (Always OFF.)"]
["Read Only",43007,"ALARM No. 65 to  80","Undefined (Always Zero.)",40285]
["Read Only",43008,"ALARM No. 80 to  96","Undefined (Always Zero.)",40286]
["Read Only",43009,"ALARM No. 97 to 112","Undefined (Always Zero.)",40287]
["Read Only",43010,"ALARM No.113 to 128","Undefined (Always Zero.)",40288]
["Read Only",43011,"FAILURE No.  1 to  16","Bit 0:START",40289]
[null,null,null,"Bit 1:⊿OP LOW"]
[null,null,null,"Bit 2:⊿P LOW"]
[null,null,null,"Bit 3:DISCHARGE PRESSURE HIGH"]
[null,null,null,"Bit 4:DISCHARGE TEMPERATURE HIGH"]
[null,null,null,"Bit 5:OIL SUPPLY TEMPERATURE HIGH"]
[null,null,null,"Bit 6:COMPRESSOR MOTOR CURRENT HIGH"]
[null,null,null,"Bit 7:OIL FILTER"]
[null,null,null,"Bit 8:INTERLOCK-2"]
[null,null,null,"Bit 9:EMERGENCY STOP"]
[null,null,null,"Bit10:OIL LEVEL LOW"]
[null,null,null,"Bit11:FINE FILTER"]
[null,null,null,"Bit12:INTERMEDIATE PRESSURE HIGH"]
[null,null,null,"Bit13:INTERLOCK"]
[null,null,null,"Bit14:LEAVING BRINE TEMPERATURE LOW"]
[null,null,null,"Bit15:INTERLOCK-3"]
["Read Only",43012,"FAILURE No. 17 to  32","Bit 0:SUCTION PRESSURE LOW",40290]
[null,null,null,"Bit 1:SUCTION PRESSURE OVER RANGE"]
[null,null,null,"Bit 2:DISCHARGE PRESSURE UNDER RANGE"]
[null,null,null,"Bit 3:OIL SUPPLY PRESSURE OVER RANGE"]
[null,null,null,"Bit 4:OIL FILTER PRESSURE OVER RANGE"]
[null,null,null,"Bit 5:SUCTION TEMPERATURE UNDER/OVER RANGE"]
[null,null,null,"Bit 6:DISCHARGE TEMPERATURE UNDER RANGE"]
[null,null,null,"Bit 7:OIL SUPPLY TEMPERATURE UNDER RANGE"]
[null,null,null,"Bit 8:INTERMEDIATE PRESSURE UNDER RANGE"]
[null,null,null,"Bit 9:INTERMEDIATE TEMPERATURE UNDER/OVER RANGE"]
[null,null,null,"Bit10:COMPRESSOR MOTOR CURRENT UNDER RANGE"]
[null,null,null,"Bit11:LEAVING BRINE TEMPERATURE OVER RANGE"]
[null,null,null,"Bit12:LOW SLIDE VALVE POSITION UNDER/OVER RANGE"]
[null,null,null,"Bit13:HIGH SLIDE VALVE POSITION UNDER/OVER RANGE"]
[null,null,null,"Bit14:CHILLER GAS TEMPERATURE1&2 UNDER/OVER RANGE"]
[null,null,null,"Bit15:SUCTION PRESSURE1&2 UNDER/OVER RANGE"]
["Read Only",43013,"FAILURE No. 33 to  48","Bit 0:Undefined (Always OFF.)",40291]
[null,null,null,"Bit 1:SUCTION SUPERHEAT LOW"]
[null,null,null,"Bit 2:SUCTION SUPERHEAT2 LOW"]
[null,null,null,"Bit 3:SUCTION PRESSURE HIGH"]
[null,null,null,"Bit 4:SUCTION TEMPERATURE HIGH"]
[null,null,null,"Bit 5:Undefined (Always OFF.)"]
[null,null,null,"Bit 6:Undefined (Always OFF.)"]
[null,null,null,"Bit 7:Undefined (Always OFF.)"]
[null,null,null,"Bit 8:Undefined (Always OFF.)"]
[null,null,null,"Bit 9:OPTION ANALOG INPUT1 LOW"]
[null,null,null,"Bit10:OPTION ANALOG INPUT1 HIGH"]
[null,null,null,"Bit11:OPTION ANALOG INPUT2 LOW"]
[null,null,null,"Bit12:OPTION ANALOG INPUT2 HIGH"]
[null,null,null,"Bit13:OPTION ANALOG INPUT3 LOW"]
[null,null,null,"Bit14:OPTION ANALOG INPUT3 HIGH"]
[null,null,null,"Bit15:OPTION ANALOG INPUT4 LOW"]
["Read Only",43014,"FAILURE No. 49 to  64","Bit 0:OPTION ANALOG INPUT4 HIGH",40292]
[null,null,null,"Bit 1:Undefined (Always OFF.)"]
[null,null,null,"Bit 2:Undefined (Always OFF.)"]
[null,null,null,"Bit 3:Undefined (Always OFF.)"]
[null,null,null,"Bit 4:Undefined (Always OFF.)"]
[null,null,null,"Bit 5:Undefined (Always OFF.)"]
[null,null,null,"Bit 6:Undefined (Always OFF.)"]
[null,null,null,"Bit 7:Undefined (Always OFF.)"]
[null,null,null,"Bit 8:Undefined (Always OFF.)"]
[null,null,null,"Bit 9:Undefined (Always OFF.)"]
[null,null,null,"Bit10:Undefined (Always OFF.)"]
[null,null,null,"Bit11:Undefined (Always OFF.)"]
[null,null,null,"Bit12:Undefined (Always OFF.)"]
[null,null,null,"Bit13:Undefined (Always OFF.)"]
[null,null,null,"Bit14:Undefined (Always OFF.)"]
[null,null,null,"Bit15:Undefined (Always OFF.)"]
["Read Only",43015,"FAILURE No. 65 to  80","Undefined (Always Zero.)",40293]
["Read Only",43016,"FAILURE No. 80 to  96","Undefined (Always Zero.)",40294]
["Read Only",43017,"FAILURE No. 97 to 112","Undefined (Always Zero.)",40295]
["Read Only",43018,"FAILURE No.113 to 128","Undefined (Always Zero.)",40296]

{"sheet":"Coil Address Sample","index":2,"n_rows":33,"n_cols":3,"rows_kept":33,"cut":false,"hidden":false,"merged":[]}
["COIL ADDRESS SAMPLE","RELATIVE MODBUS ADDRESS","DESCRIPTION"]
["B112:000/00",513,"_RMT_COMP_START"]
["B112:000/01",514,"_RMT_COMP_IMMEDIATE_STOP"]
["B112:000/02",515,"_RMT_COMP_FULL_LOAD"]
["B112:000/03",516,"_RMT_COMP_LOAD_LIMIT"]
["B112:000/04","RESERVED","RESERVED"]
["B112:000/05",518,"_RMT_CHILL_LBT_100PERCENT"]
["B112:000/06","RESERVED","RESERVED"]
["B112:000/07","RESERVED","RESERVED"]
["B112:000/08","RESERVED","RESERVED"]
["B112:000/09","RESERVED","RESERVED"]
["B112:000/10","RESERVED","RESERVED"]
["B112:000/11","RESERVED","RESERVED"]
["B112:000/12","RESERVED","RESERVED"]
["B112:000/13","RESERVED","RESERVED"]
["B112:000/14","RESERVED","RESERVED"]
["B112:000/15","RESERVED","RESERVED"]
["B112:001/00","RESERVED","RESERVED"]
["B112:001/01","RESERVED","RESERVED"]
["B112:001/02","RESERVED","RESERVED"]
["B112:001/03","RESERVED","RESERVED"]
["B112:001/04","RESERVED","RESERVED"]
["B112:001/05","RESERVED","RESERVED"]
["B112:001/06","RESERVED","RESERVED"]
["B112:001/07","RESERVED","RESERVED"]
["B112:001/08","RESERVED","RESERVED"]
["B112:001/09","RESERVED","RESERVED"]
["B112:001/10","RESERVED","RESERVED"]
["B112:001/11","RESERVED","RESERVED"]
["B112:001/12","RESERVED","RESERVED"]
["B112:001/13","RESERVED","RESERVED"]
["B112:001/14","RESERVED","RESERVED"]
["B112:001/15",576,"_RMT_CLEAR_ALARM"]

{"sheet":"File and Slave Number","index":3,"n_rows":33,"n_cols":3,"rows_kept":33,"cut":false,"hidden":false,"merged":[]}
["MYPRO Touch Slave Address","AddresType","File Number at RSlogix500"]
[1,"WORD","N110:000"]
[1,"WORD","N111:000"]
[1,"COIL","B112:000"]
[1,"COIL","B112:001"]
[1,"WORD","N120:000"]
[1,"WORD","N121:000"]
[1,"COIL","B122:000"]
[1,"COIL","B122:001"]
[3,"WORD","N130:000"]
[3,"WORD","N131:000"]
[3,"COIL","B132:000"]
[3,"COIL","B132:001"]
[4,"WORD","N140:000"]
[4,"WORD","N141:000"]
[4,"COIL","B142:000"]
[4,"COIL","B142:001"]
[5,"WORD","N150:000"]
[5,"WORD","N151:000"]
[5,"COIL","B152:000"]
[5,"COIL","B152:001"]
[6,"WORD","N160:000"]
[6,"WORD","N161:000"]
[6,"COIL","B162:000"]
[6,"COIL","B162:001"]
[7,"WORD","N170:000"]
[7,"WORD","N171:000"]
[7,"COIL","B172:000"]
[7,"COIL","B172:001"]
[8,"WORD","N180:000"]
[8,"WORD","N181:000"]
[8,"COIL","B182:000"]
[8,"COIL","B182:001"]