{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["Comm Addresses(MT01)","LOW16 & HIGH 16 BITS","Alarm & Failure Bit Sheet"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Comm Addresses(MT01)","index":0,"n_rows":465,"n_cols":8,"rows_kept":465,"cut":false,"hidden":false,"merged":[]}
["ADDRESS TYPE","READ/WRITE","RELATIVE MODBUS","RELATIVE RSLOGIX5000 ADDRESS",null,"DESCRIPTION","DATA"]
["WORD","READ",43001,{"$f":"CONCATENATE(\"MTP01_N000_127[\",E2,\"]\")","v":"MTP01_N000_127[0]"},0,"DI/O Low 16bits (See Detail Tab for Description)","DI/O01(b0)~DI/O16(b15)"]
["WORD","READ",43002,{"$f":"CONCATENATE(\"MTP01_N000_127[\",E3,\"]\")","v":"MTP01_N000_127[1]"},1,"DI/O High 16bits (See Detail Tab for Description)","DI/O17(b0)~DI/O32(b15)"]
["WORD","READ",43003,{"$f":"CONCATENATE(\"MTP01_N000_127[\",E4,\"]\")","v":"MTP01_N000_127[2]"},2,"ALARM No.  1 to  16","No.  1(b0)~No. 16(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43004,"MTP01_N000_127[3]",3,"ALARM No. 17 to  32","No. 17(b0)~No. 32(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43005,"MTP01_N000_127[4]",4,"ALARM No. 33 to  48","No. 33(b0)~No. 48(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43006,"MTP01_N000_127[5]",5,"ALARM No. 49 to  64","No. 49(b0)~No. 64(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43007,"MTP01_N000_127[6]",6,"ALARM No. 65 to  80","No. 65(b0)~No. 80(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43008,"MTP01_N000_127[7]",7,"ALARM No. 80 to  96","No. 81(b0)~No. 96(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43009,"MTP01_N000_127[8]",8,"ALARM No. 97 to 112","No. 97(b0)~No.112(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43010,"MTP01_N000_127[9]",9,"ALARM No.113 to 128","No.113(b0)~No.128(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43011,"MTP01_N000_127[10]",10,"FAILURE No.  1 to  16","No.  1(b0)~No. 16(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43012,"MTP01_N000_127[11]",11,"FAILURE No. 17 to  32","No. 17(b0)~No. 32(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43013,"MTP01_N000_127[12]",12,"FAILURE No. 33 to  48","No. 33(b0)~No. 48(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43014,"MTP01_N000_127[13]",13,"FAILURE No. 49 to  64","No. 49(b0)~No. 64(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43015,"MTP01_N000_127[14]",14,"FAILURE No. 65 to  80","No. 65(b0)~No. 80(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43016,"MTP01_N000_127[15]",15,"FAILURE No. 80 to  96","No. 81(b0)~No. 96(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43017,"MTP01_N000_127[16]",16,"FAILURE No. 97 to 112","No. 97(b0)~No.112(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43018,"MTP01_N000_127[17]",17,"FAILURE No.113 to 128","No.113(b0)~No.128(b15)","Refer ALARM&FAILURE Bits Sheet"]
["WORD","READ",43019,"MTP01_N000_127[18]",18,"AI01","Local Suction Pressure","Industrial Unit X 10^n"]
["WORD","READ",43020,"MTP01_N000_127[19]",19,"AI02","Discharge Pressure","Industrial Unit X 10^n"]
["WORD","READ",43021,"MTP01_N000_127[20]",20,"AI03","Oil Supply Pressure","Industrial Unit X 10^n"]
["WORD","READ",43022,"MTP01_N000_127[21]",21,"AI04","After Filter Pressure","Industrial Unit X 10^n"]
["WORD","READ",43023,"MTP01_N000_127[22]",22,"AI05","Suction Temperature","Industrial Unit X 10^n"]
["WORD","READ",43024,"MTP01_N000_127[23]",23,"AI06","Discharge Temperature","Industrial Unit X 10^n"]
["WORD","READ",43025,"MTP01_N000_127[24]",24,"AI07","Oil Supply Temperature","Industrial Unit X 10^n"]
["WORD","READ",43026,"MTP01_N000_127[25]",25,"AI08","Oil Separator Temperature","Industrial Unit X 10^n"]
["WORD","READ",43027,"MTP01_N000_127[26]",26,"AI09","Intermediate Pressure","Industrial Unit X 10^n"]
["WORD","READ",43028,"MTP01_N000_127[27]",27,"AI10","Intermediate Temperature","Industrial Unit X 10^n"]
["WORD","READ",43029,"MTP01_N000_127[28]",28,"AI11","Chiller Liquid Level","Industrial Unit X 10^n"]
["WORD","READ",43030,"MTP01_N000_127[29]",29,"AI12","Compressor Motor Electric Current","Industrial Unit X 10^n"]
["WORD","READ",43031,"MTP01_N000_127[30]",30,"AI13","Chiller Inlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",43032,"MTP01_N000_127[31]",31,"AI14","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",43033,"MTP01_N000_127[32]",32,"AI15","Low Stage Slide Valve Position","Industrial Unit X 10^n"]
["WORD","READ",43034,"MTP01_N000_127[33]",33,"AI16","High Satge Slide Valve position/Vi Port Slide Valve Position","Industrial Unit X 10^n"]
["WORD","READ",43035,"MTP01_N000_127[34]",34,"AI17","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43036,"MTP01_N000_127[35]",35,"AI18","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43037,"MTP01_N000_127[36]",36,"AI19","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43038,"MTP01_N000_127[37]",37,"AI20","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43039,"MTP01_N000_127[38]",38,"AI21","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43040,"MTP01_N000_127[39]",39,"AI22","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43041,"MTP01_N000_127[40]",40,"AI23","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43042,"MTP01_N000_127[41]",41,"AI24","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43043,"MTP01_N000_127[42]",42,"AI25","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43044,"MTP01_N000_127[43]",43,"AI26","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43045,"MTP01_N000_127[44]",44,"AI27","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43046,"MTP01_N000_127[45]",45,"AI28","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43047,"MTP01_N000_127[46]",46,"AI29","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43048,"MTP01_N000_127[47]",47,"AI30","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43049,"MTP01_N000_127[48]",48,"AI31","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43050,"MTP01_N000_127[49]",49,"AI32","Real Analog Input","Industrial Unit X 10^n"]
["WORD","READ",43051,"MTP01_N000_127[50]",50,"AI65","Oil Differential Pressure(DP - OP) (n=2)","Industrial Unit X 10^n"]
["WORD","READ",43052,"MTP01_N000_127[51]",51,"AI66","Filter Diffirential Pressure(DP - AFP) (n=2)","Industrial Unit X 10^n"]
["WORD","READ",43053,"MTP01_N000_127[52]",52,"AI67","Differentila Pressure (n=2)\nSingle(AFP - SP),Compound(AFP - IP)","Industrial Unit X 10^n"]
["WORD","READ",43054,"MTP01_N000_127[53]",53,"AI68","Suction Superheat(n=1)","Industrial Unit X 10^n"]
["WORD","READ",43055,"MTP01_N000_127[54]",54,"AI69","Intermediate Superheat(n=1)","Industrial Unit X 10^n"]
["WORD","READ",43056,"MTP01_N000_127[55]",55,"AI70","Discharge Superheat(n=1)","Industrial Unit X 10^n"]
["WORD","READ",43057,"MTP01_N000_127[56]",56,"AI71","Ratio:DP÷SP(n=2)","Industrial Unit X 10^n"]
["WORD","READ",43058,"MTP01_N000_127[57]",57,"AI72","Calculated Vi(n=2)","Industrial Unit X 10^n"]
["WORD","READ",43059,"MTP01_N000_127[58]",58,"AI73","Current Vi 2.63/3.65/5.80, 2.50/3.50/5.00(n=2)","Industrial Unit X 10^n"]
["WORD","READ",43060,"MTP01_N000_127[59]",59,"AI74","Capacity/VFD Output(n=1)","Industrial Unit X 10^n"]
["WORD","READ",43061,"MTP01_N000_127[60]",60,"AI75","(Low Stage)Slide Valave Percent(n=1)","Industrial Unit X 10^n"]
["WORD","READ",43062,"MTP01_N000_127[61]",61,"AI76","AUTO STAGE Target-Pressure(n=3)","Industrial Unit X 10^n"]
["WORD","READ",43063,"MTP01_N000_127[62]",62,"AI77","Oil Differential Pressure2(OP2-DP)(n=2)","Industrial Unit X 10^n"]
["WORD","READ",43064,"MTP01_N000_127[63]",63,"AI78","Suction Superheat2(n=1)","Industrial Unit X 10^n"]
["WORD","READ",43065,"MTP01_N000_127[64]",64,"AI79","Fine Filter Differential Pressure(DP - AFFP) (n=2)","Industrial Unit X 10^n"]
["WORD","READ",43066,"MTP01_N000_127[65]",65,"AI80","AUTO STAGE Tearget-Temperature(n=1)","Industrial Unit X 10^n"]
["WORD","READ",43067,{"$f":"CONCATENATE(\"MTP01_N000_127[\",E68,\"]\")","v":"MTP01_N000_127[66]"},66,"PID 1/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43068,"MTP01_N000_127[67]",67,"PID 1/16PV","Local/System Suction/Discharge Pressure","Industrial Unit X 10^n"]
["WORD","READ",43069,"MTP01_N000_127[68]",68,"PID 1/16MV","Output of Low Stage Slide Valve Control on Pressure/Combined","0.0~100.0%:0~1000"]
["WORD","READ",43070,"MTP01_N000_127[69]",69,"PID 2/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43071,"MTP01_N000_127[70]",70,"PID 2/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",43072,"MTP01_N000_127[71]",71,"PID 2/16MV","Output of Low Stage Slide Valve Control on Temperature","0.0~100.0%:0~1000"]
["WORD","READ",43073,"MTP01_N000_127[72]",72,"PID 3/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43074,"MTP01_N000_127[73]",73,"PID 3/16PV","Suction Superheat","Industrial Unit X 10^n"]
["WORD","READ",43075,"MTP01_N000_127[74]",74,"PID 3/16MV","Output of Chiller Expansion Vale Control","0.0~100.0%:0~1000"]
["WORD","READ",43076,"MTP01_N000_127[75]",75,"PID 4/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43077,"MTP01_N000_127[76]",76,"PID 4/16PV","Local Suction Pressure","Industrial Unit X 10^n"]
["WORD","READ",43078,"MTP01_N000_127[77]",77,"PID 4/16MV","Output of Limitation of Cheller Expansion Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",43079,"MTP01_N000_127[78]",78,"PID 5/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43080,"MTP01_N000_127[79]",79,"PID 5/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",43081,"MTP01_N000_127[80]",80,"PID 5/16MV","Output of Limitation of Cheller Expansion Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",43082,"MTP01_N000_127[81]",81,"PID 6/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43083,"MTP01_N000_127[82]",82,"PID 6/16PV","Intermediate Superheat","Industrial Unit X 10^n"]
["WORD","READ",43084,"MTP01_N000_127[83]",83,"PID 6/16MV","Output of Economizer/Inter Cooler Expansion Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",43085,"MTP01_N000_127[84]",84,"PID 7/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43086,"MTP01_N000_127[85]",85,"PID 7/16PV","Discharge Temperature/Superheat","Industrial Unit X 10^n"]
["WORD","READ",43087,"MTP01_N000_127[86]",86,"PID 7/16MV","Output of Liquid Injection Control","0.0~100.0%:0~1000"]
["WORD","READ",43088,"MTP01_N000_127[87]",87,"PID 8/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43089,"MTP01_N000_127[88]",88,"PID 8/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",43090,"MTP01_N000_127[89]",89,"PID 8/16MV","Output of Brine Flow Control","0.0~100.0%:0~1000"]
["WORD","READ",43091,"MTP01_N000_127[90]",90,"PID 9/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43092,"MTP01_N000_127[91]",91,"PID 9/16PV","Local/System Discharge pressure","Industrial Unit X 10^n"]
["WORD","READ",43093,"MTP01_N000_127[92]",92,"PID 9/16MV","Output of Condenser Fan/Pump Control","0.0~100.0%:0~1000"]
["WORD","READ",43094,"MTP01_N000_127[93]",93,"PID10/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43095,"MTP01_N000_127[94]",94,"PID10/16PV","Intermediate Pressure","Industrial Unit X 10^n"]
["WORD","READ",43096,"MTP01_N000_127[95]",95,"PID10/16MV","Output of High Stage Slide Valve Control","0.0~100.0%:0~1000"]
["WORD","READ",43097,"MTP01_N000_127[96]",96,"PID11/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43098,"MTP01_N000_127[97]",97,"PID11/16PV","Local/System Suction/Discharge Pressure","Industrial Unit X 10^n"]
["WORD","READ",43099,"MTP01_N000_127[98]",98,"PID11/16MV","Output of Compressor Motor on Pressure/Combined","0.0~100.0%:0~1000"]
["WORD","READ",43100,"MTP01_N000_127[99]",99,"PID12/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43101,"MTP01_N000_127[100]",100,"PID12/16PV","Chiller Outlet Temperature","Industrial Unit X 10^n"]
["WORD","READ",43102,"MTP01_N000_127[101]",101,"PID12/16MV","Output of Compressor Motor on Temperature","0.0~100.0%:0~1000"]
["WORD","READ",43103,"MTP01_N000_127[102]",102,"PID13/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43104,"MTP01_N000_127[103]",103,"PID13/16PV","Suction Superheat2","Industrial Unit X 10^n"]
["WORD","READ",43105,"MTP01_N000_127[104]",104,"PID13/16MV","Output of Chiller Expansion Vale2 Control","0.0~100.0%:0~1000"]
["WORD","READ",43106,"MTP01_N000_127[105]",105,"PID14/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43107,"MTP01_N000_127[106]",106,"PID14/16PV","Suction Pressure2","Industrial Unit X 10^n"]
["WORD","READ",43108,"MTP01_N000_127[107]",107,"PID14/16MV","Output of Limitation of Cheller Expansion Valve2 Control","0.0~100.0%:0~1000"]
["WORD","READ",43109,"MTP01_N000_127[108]",108,"PID15/16SV",null,"Industrial Unit X 10^n"]
["WORD","READ",43110,"MTP01_N000_127[109]",109,"PID15/16PV","Chiller Liquid Level","Industrial Unit X 10^n"]
["WORD","READ",43111,"MTP01_N000_127[110]",110,"PID15/16MV","Output of Chiller Liquid Level Control","0.0~100.0%:0~1000"]
["WORD","READ",43112,"MTP01_N000_127[111]",111,"PID16/16SV","Undefined","Industrial Unit X 10^n"]
["WORD","READ",43113,"MTP01_N000_127[112]",112,"PID16/16PV","Undefined","Industrial Unit X 10^n"]
["WORD","READ",43114,"MTP01_N000_127[113]",113,"PID16/16MV","Undefined","0.0~100.0%:0~1000"]
["WORD","READ",43115,"MTP01_N000_127[114]",114,"RUN TIME Low","Low 16bits of 32bits Hours"]
["WORD","READ",43116,"MTP01_N000_127[115]",115,"RUN TIME High","High 16bits of 32bits Hours","RUN TIME = (R43065) + 65536 X (R43066)"]
["WORD","READ",43117,"MTP01_N000_127[116]",116,"TOTAL RUN TIME Low","Low 16bits of 32bits Hours"]
["WORD","READ",43118,"MTP01_N000_127[117]",117,"TOTAL RUN TIME High","High 16bits of 32bits Hours","RUN TIME = (R43067) + 65536 X (R43068)"]
["WORD","READ",43119,"MTP01_N000_127[118]",118,"RTC","Week","0(SUN.) to Six(SAT.)"]
["WORD","READ",43120,"MTP01_N000_127[119]",119,"RTC","Month","1 to 12"]
["WORD","READ",43121,"MTP01_N000_127[120]",120,"RTC","Day","1 to 31"]
["WORD","READ",43122,"MTP01_N000_127[121]",121,"RTC","Year","A.D. Four digits."]
["WORD","READ",43123,"MTP01_N000_127[122]",122,"RTC","Hour","0 to 23"]
["WORD","READ",43124,"MTP01_N000_127[123]",123,"RTC","Minute","0 to 59"]
["WORD","READ",43125,"MTP01_N000_127[124]",124,"RTC","Second","0 to 59"]
["WORD","READ",43126,"MTP01_N000_127[125]",125,"Undefined"]
["WORD","READ",43127,"MTP01_N000_127[126]",126,"Undefined"]
["WORD","READ",43128,"MTP01_N000_127[127]",127,"Undefined"]
["WORD","READ/WRITE",43129,{"$f":"CONCATENATE(\"MTP01_N128_159[\",E130,\"]\")","v":"MTP01_N128_159[0]"},0,"CUT IN Set Point","Pressure or Temperature","Industrial Unit X 10^n"]
["WORD","READ/WRITE",43130,{"$f":"CONCATENATE(\"MTP01_N128_159[\",E131,\"]\")","v":"MTP01_N128_159[1]"},1,"CUT OUT Set Point","Pressure or Temperature"]
["WORD","READ/WRITE",43131,"MTP01_N128_159[2]",2,"Pressure Set Point of CAPACITY CONTROL"]
["WORD","READ/WRITE",43132,"MTP01_N128_159[3]",3,"Temperature Set Point of CAPACITY CONTROL"]
["WORD","READ/WRITE",43133,"MTP01_N128_159[4]",4,"Capacity Set Point",null,"0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43134,"MTP01_N128_159[5]",5,"Undefined"]
["WORD","READ/WRITE",43135,"MTP01_N128_159[6]",6,"Undefined"]
["WORD","READ/WRITE",43136,"MTP01_N128_159[7]",7,"Undefined"]
["WORD","READ/WRITE",43137,"MTP01_N128_159[8]",8,"Undefined"]
["WORD","READ/WRITE",43138,"MTP01_N128_159[9]",9,"Undefined"]
["WORD","READ/WRITE",43139,"MTP01_N128_159[10]",10,"Undefined"]
["WORD","READ/WRITE",43140,"MTP01_N128_159[11]",11,"Undefined"]
["WORD","READ/WRITE",43141,"MTP01_N128_159[12]",12,"Undefined"]
["WORD","READ/WRITE",43142,"MTP01_N128_159[13]",13,"Undefined"]
["WORD","READ/WRITE",43143,"MTP01_N128_159[14]",14,"Undefined"]
["WORD","READ/WRITE",43144,"MTP01_N128_159[15]",15,"Undefined"]
["WORD","READ/WRITE",43145,"MTP01_N128_159[16]",16,"PID 1/16MVL","Set Point MVL of CAPACITY CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43146,"MTP01_N128_159[17]",17,"PID 1/16MVH","Set Point MVH of CAPACITY CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43147,"MTP01_N128_159[18]",18,"PID 2/16MVL","Set Point MVL of CAPACITY CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43148,"MTP01_N128_159[19]",19,"PID 2/16MVH","Set Point MVH of CAPACITY CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43149,"MTP01_N128_159[20]",20,"PID11/16MVL","Set Point MVL of VFD COMPRESSOR CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43150,"MTP01_N128_159[21]",21,"PID11/16MVH","Set Point MVH of VFD COMPRESSOR CONTROLLER on Pressure","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43151,"MTP01_N128_159[22]",22,"PID12/16MVL","Set Point MVL of VFD COMPRESSOR CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43152,"MTP01_N128_159[23]",23,"PID12/16MVH","Set Point MVH of VFD COMPRESSOR CONTROLLER on Temperature","0.0~100.0%:0~1000"]
["WORD","READ/WRITE",43153,"MTP01_N128_159[24]",24,"MODE SELECT","OPERATION MODE>OPERATION","(0):LOCAL\n,1:REMOTE\n,2:COMM\n,3:AUTO STAGE\n,4:Not Use\n,5:AUTO STAGE REMOTE\n,6:AUTO STAGE COMM"]
["WORD","READ/WRITE",43154,"MTP01_N128_159[25]",25,"AUTO START SELECT","OPERATION MODE>COMPRESSOR AUTO START/STOP ","0:NO,(1):YES"]
["WORD","READ/WRITE",43155,"MTP01_N128_159[26]",26,"SET POINT No. SELSECT","SET POINTS>SCHEDULER>CUT IN/CUT OUT","(0):SETPOINT #1\n,1:SETPOINT #2\n,2:SETPOINT #3\n,3:SETPOINT #4\n,4:SCHEDULER\n,5:COMM"]
["WORD","READ/WRITE",43156,"MTP01_N128_159[27]",27,"SET POINT No. SELSECT","SET POINTS>SCHEDULER>CONTROL TARGET","(0):SETPOINT #1\n,1:SETPOINT #2\n,2:SETPOINT #3\n,3:SETPOINT #4\n,4:SCHEDULER\n,5:COMM"]
["WORD","READ/WRITE",43157,"MTP01_N128_159[28]",28,"ALARM/FAILURE SELSCT","OPERATION MODE>ALARM/FAILURE","(0):SET POINT#1,1:SET POINT#2"]
["WORD","READ/WRITE",43158,"MTP01_N128_159[29]",29,"CAPACITY CONTROL SELECT","CAPACITY CONTROL>MONITOR>OPERATION","(0):MANUAL\n,1:AUTO\n,2:REMOTE DIGITAL\n,3:REMOTE ANALOG\n,4:COMM"]
["WORD","READ/WRITE",43159,"MTP01_N128_159[30]",30,"VFD COMPRESSOR CONTROL SELECT","VFD COMPRESSOR CONTROL>MONITOR>OPERATION","(0):MANUAL\n,1:AUTO\n,2:REMOTE DIGITAL\n,3:REMOTE ANALOG\n,4:COMM"]
["WORD","READ/WRITE",43160,"MTP01_N128_159[31]",31,null,"CAPACITY CONTROL>MVL%/MVH% BY COMM","(0):DISABLE,1:ENABLE"]
["WORD","READ/WRITE",43161,"MTP01_N128_159[32]",32,"Undefined"]
["WORD","READ/WRITE",43162,"MTP01_N128_159[33]",33,"Undefined"]
["WORD","READ/WRITE",43163,"MTP01_N128_159[34]",34,"Undefined"]
["WORD","READ/WRITE",43164,"MTP01_N128_159[35]",35,"Undefined"]
["WORD","READ/WRITE",43165,"MTP01_N128_159[36]",36,"Undefined"]
["WORD","READ/WRITE",43166,"MTP01_N128_159[37]",37,"Undefined"]
["WORD","READ/WRITE",43167,"MTP01_N128_159[38]",38,"Undefined"]
["WORD","READ/WRITE",43168,"MTP01_N128_159[39]",39,"Undefined"]
["WORD","READ/WRITE",43169,"MTP01_N128_159[40]",40,"Undefined"]
["WORD","READ/WRITE",43170,"MTP01_N128_159[41]",41,"Undefined"]
["WORD","READ/WRITE",43171,"MTP01_N128_159[42]",42,"Undefined"]
["WORD","READ/WRITE",43172,"MTP01_N128_159[43]",43,"Undefined"]
["WORD","READ/WRITE",43173,"MTP01_N128_159[44]",44,"Undefined"]
["WORD","READ/WRITE",43174,"MTP01_N128_159[45]",45,"Undefined"]
["WORD","READ/WRITE",43175,"MTP01_N128_159[46]",46,"Undefined"]
["WORD","READ/WRITE",43176,"MTP01_N128_159[47]",47,"Undefined"]
["WORD","READ/WRITE",43177,"MTP01_N128_159[48]",48,"Undefined"]
["WORD","READ/WRITE",43178,"MTP01_N128_159[49]",49,"Undefined"]
["WORD","READ/WRITE",43179,"MTP01_N128_159[50]",50,"Undefined"]
["WORD","READ/WRITE",43180,"MTP01_N128_159[51]",51,"Undefined"]
["WORD","READ/WRITE",43181,"MTP01_N128_159[52]",52,"Undefined"]
["WORD","READ/WRITE",43182,"MTP01_N128_159[53]",53,"Undefined"]
["WORD","READ/WRITE",43183,"MTP01_N128_159[54]",54,"Undefined"]
["WORD","READ/WRITE",43184,"MTP01_N128_159[55]",55,"Undefined"]
["WORD","READ/WRITE",43185,"MTP01_N128_159[56]",56,"Undefined"]
["WORD","READ/WRITE",43186,"MTP01_N128_159[57]",57,"Undefined"]
["WORD","READ/WRITE",43187,"MTP01_N128_159[58]",58,"Undefined"]
["WORD","READ/WRITE",43188,"MTP01_N128_159[59]",59,"Undefined"]
["WORD","READ/WRITE",43189,"MTP01_N128_159[60]",60,"Undefined"]
["WORD","READ/WRITE",43190,"MTP01_N128_159[61]",61,"Undefined"]
["WORD","READ/WRITE",43191,"MTP01_N128_159[62]",62,"Undefined"]
["WORD","READ/WRITE",43192,"MTP01_N128_159[63]",63,"Undefined"]
["WORD","READ/WRITE",43193,"MTP01_N128_159[64]",64,"Reserved"]
["WORD","READ/WRITE",43194,{"$f":"CONCATENATE(\"MTP01_N128_159[\",E195,\"]\")","v":"MTP01_N128_159[65]"},65,"Reserved"]
["WORD","READ/WRITE",43195,"MTP01_N128_159[66]",66,"Reserved"]
["WORD","READ/WRITE",43196,"MTP01_N128_159[67]",67,"Reserved"]
["WORD","READ/WRITE",43197,"MTP01_N128_159[68]",68,"Reserved"]
["WORD","READ/WRITE",43198,"MTP01_N128_159[69]",69,"Reserved"]
["WORD","READ/WRITE",43199,"MTP01_N128_159[70]",70,"Reserved"]
["WORD","READ/WRITE",43200,"MTP01_N128_159[71]",71,"Reserved"]
["WORD","READ/WRITE",43201,"MTP01_N128_159[72]",72,"Reserved"]
["WORD","READ/WRITE",43202,"MTP01_N128_159[73]",73,"Reserved"]
["WORD","READ/WRITE",43203,"MTP01_N128_159[74]",74,"Reserved"]
["WORD","READ/WRITE",43204,"MTP01_N128_159[75]",75,"Reserved"]
["WORD","READ/WRITE",43205,"MTP01_N128_159[76]",76,"Reserved"]
["WORD","READ/WRITE",43206,"MTP01_N128_159[77]",77,"Reserved"]
["WORD","READ/WRITE",43207,"MTP01_N128_159[78]",78,"Reserved"]
["WORD","READ/WRITE",43208,"MTP01_N128_159[79]",79,"Reserved"]
["WORD","READ/WRITE",43209,"MTP01_N128_159[80]",80,"Reserved"]
["WORD","READ/WRITE",43210,"MTP01_N128_159[81]",81,"Reserved"]
["WORD","READ/WRITE",43211,"MTP01_N128_159[82]",82,"Reserved"]
["WORD","READ/WRITE",43212,"MTP01_N128_159[83]",83,"Reserved"]
["WORD","READ/WRITE",43213,"MTP01_N128_159[84]",84,"Reserved"]
["WORD","READ/WRITE",43214,"MTP01_N128_159[85]",85,"Reserved"]
["WORD","READ/WRITE",43215,"MTP01_N128_159[86]",86,"Reserved"]
["WORD","READ/WRITE",43216,"MTP01_N128_159[87]",87,"Reserved"]
["WORD","READ/WRITE",43217,"MTP01_N128_159[88]",88,"Reserved"]
["WORD","READ/WRITE",43218,"MTP01_N128_159[89]",89,"Reserved"]
["WORD","READ/WRITE",43219,"MTP01_N128_159[90]",90,"Reserved"]
["WORD","READ/WRITE",43220,"MTP01_N128_159[91]",91,"Reserved"]
["WORD","READ/WRITE",43221,"MTP01_N128_159[92]",92,"Reserved"]
["WORD","READ/WRITE",43222,"MTP01_N128_159[93]",93,"Reserved"]
["WORD","READ/WRITE",43223,"MTP01_N128_159[94]",94,"Reserved"]
["WORD","READ/WRITE",43224,"MTP01_N128_159[95]",95,"Reserved"]
["WORD","READ/WRITE",43225,"MTP01_N128_159[96]",96,"Reserved"]
["WORD","READ/WRITE",43226,"MTP01_N128_159[97]",97,"Reserved"]
["WORD","READ/WRITE",43227,"MTP01_N128_159[98]",98,"Reserved"]
["WORD","READ/WRITE",43228,"MTP01_N128_159[99]",99,"Reserved"]
["WORD","READ/WRITE",43229,"MTP01_N128_159[100]",100,"Reserved"]
["WORD","READ/WRITE",43230,"MTP01_N128_159[101]",101,"Reserved"]
["WORD","READ/WRITE",43231,"MTP01_N128_159[102]",102,"Reserved"]
["WORD","READ/WRITE",43232,"MTP01_N128_159[103]",103,"Reserved"]
["WORD","READ/WRITE",43233,"MTP01_N128_159[104]",104,"Reserved"]
["WORD","READ/WRITE",43234,"MTP01_N128_159[105]",105,"Reserved"]
["WORD","READ/WRITE",43235,"MTP01_N128_159[106]",106,"Reserved"]
["WORD","READ/WRITE",43236,"MTP01_N128_159[107]",107,"Reserved"]
["WORD","READ/WRITE",43237,"MTP01_N128_159[108]",108,"Reserved"]
["WORD","READ/WRITE",43238,"MTP01_N128_159[109]",109,"Reserved"]
["WORD","READ/WRITE",43239,"MTP01_N128_159[110]",110,"Reserved"]
["WORD","READ/WRITE",43240,"MTP01_N128_159[111]",111,"Reserved"]
["WORD","READ/WRITE",43241,"MTP01_N128_159[112]",112,"Reserved"]
["WORD","READ/WRITE",43242,"MTP01_N128_159[113]",113,"Reserved"]
["WORD","READ/WRITE",43243,"MTP01_N128_159[114]",114,"Reserved"]
["WORD","READ/WRITE",43244,"MTP01_N128_159[115]",115,"Reserved"]
["WORD","READ/WRITE",43245,"MTP01_N128_159[116]",116,"Reserved"]
["WORD","READ/WRITE",43246,"MTP01_N128_159[117]",117,"Reserved"]
["WORD","READ/WRITE",43247,"MTP01_N128_159[118]",118,"Reserved"]
["WORD","READ/WRITE",43248,"MTP01_N128_159[119]",119,"Reserved"]
["WORD","READ/WRITE",43249,"MTP01_N128_159[120]",120,"Reserved"]
["WORD","READ/WRITE",43250,"MTP01_N128_159[121]",121,"Reserved"]
["WORD","READ/WRITE",43251,"MTP01_N128_159[122]",122,"Reserved"]
["WORD","READ/WRITE",43252,"MTP01_N128_159[123]",123,"Reserved"]
["WORD","READ/WRITE",43253,"MTP01_N128_159[124]",124,"Reserved"]
["WORD","READ/WRITE",43254,"MTP01_N128_159[125]",125,"Reserved"]
["WORD","READ/WRITE",43255,"MTP01_N128_159[126]",126,"Reserved"]
["WORD","READ/WRITE",43256,"MTP01_N128_159[127]",127,"Reserved"]
["WORD","READ",43257,{"$f":"CONCATENATE(\"MTP01_N256_383[\",E258,\"]\")","v":"MTP01_N256_383[0]"},0,"STATUS","CURRENT CUT-IN SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",43258,{"$f":"CONCATENATE(\"MTP01_N256_383[\",E259,\"]\")","v":"MTP01_N256_383[1]"},1,"STATUS","CURRENT PRESSURE CONTROL SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",43259,"MTP01_N256_383[2]",2,"STATUS","CURRENT TEMPERATURE CONTROL SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",43260,"MTP01_N256_383[3]",3,"STATUS","CURRENT CUT-OUT SET POINT","RANGE LOW TO HIGH: 0 TO 4095"]
["WORD","READ",43261,"MTP01_N256_383[4]",4,"STATUS","ALARM STATUS","(0) NO ALARM - NO FAILURE, 1: ALARM - NO FAILURE, 2: NO ALARM -FAILURE, 3: ALARM - FAILURE"]
["WORD","READ",43262,"MTP01_N256_383[5]",5,"STATUS","COMPRESSOR OPERATION MODE","(0) LOCAL-OFF, 1: LOCAL-ON, 2: REMOTE-OFF, 3: REMOTE-ON, 4: COMM-OFF, 5: COMM-ON, 6:AUTO STAGE-OFF, 7:AUTO STAGE-ON"]
["WORD","READ",43263,"MTP01_N256_383[6]",6,"STATUS","COMPRESSOR STATUS","(0) STOP, 1: ANTI CYCLE, 2: AUTO STOP, 3: CUT IN, 4: SYSTEM START, 5: OIL PUMP START, 6: PRE START, 7: START, 8: RUN, 9: CUT OUT, 10: PUMP OUT"]
["WORD","READ",43264,"MTP01_N256_383[7]",7,"STATUS","DELAY TIMERS TO TIME UP","SECONDS"]
["WORD","READ",43265,"MTP01_N256_383[8]",8,"STATUS","VFD COMPRESSOR REVOLUTION (MOTOR SPEED)","RPM/HZ"]
["WORD","READ",43266,"MTP01_N256_383[9]",9,"STATUS","VFD CONDENSER REVOLUTION","RPM/HZ"]
["WORD","READ",43267,"MTP01_N256_383[10]",10,"Reserved","Reserved"]
["WORD","READ",43268,"MTP01_N256_383[11]",11,"Reserved","Reserved"]
["WORD","READ",43269,"MTP01_N256_383[12]",12,"Reserved","Reserved"]
["WORD","READ",43270,"MTP01_N256_383[13]",13,"Reserved","Reserved"]
["WORD","READ",43271,"MTP01_N256_383[14]",14,"Reserved","Reserved"]
["WORD","READ",43272,"MTP01_N256_383[15]",15,"Reserved","Reserved"]
["WORD","READ",43273,"MTP01_N256_383[16]",16,"Reserved","Reserved"]
["WORD","READ",43274,"MTP01_N256_383[17]",17,"Reserved","Reserved"]
["WORD","READ",43275,"MTP01_N256_383[18]",18,"Reserved","Reserved"]
["WORD","READ",43276,"MTP01_N256_383[19]",19,"Reserved","Reserved"]
["WORD","READ",43277,"MTP01_N256_383[20]",20,"Reserved","Reserved"]
["WORD","READ",43278,"MTP01_N256_383[21]",21,"Reserved","Reserved"]
["WORD","READ",43279,"MTP01_N256_383[22]",22,"Reserved","Reserved"]
["WORD","READ",43280,"MTP01_N256_383[23]",23,"Reserved","Reserved"]
["WORD","READ",43281,"MTP01_N256_383[24]",24,"Reserved","Reserved"]
["WORD","READ",43282,"MTP01_N256_383[25]",25,"Reserved","Reserved"]
["WORD","READ",43283,"MTP01_N256_383[26]",26,"Reserved","Reserved"]
["WORD","READ",43284,"MTP01_N256_383[27]",27,"Reserved","Reserved"]
["WORD","READ",43285,"MTP01_N256_383[28]",28,"Reserved","Reserved"]
["WORD","READ",43286,"MTP01_N256_383[29]",29,"Reserved","Reserved"]
["WORD","READ",43287,"MTP01_N256_383[30]",30,"Reserved","Reserved"]
["WORD","READ",43288,"MTP01_N256_383[31]",31,"Reserved","Reserved"]
["WORD","READ",43289,"MTP01_N256_383[32]",32,"Reserved","Reserved"]
["WORD","READ",43290,"MTP01_N256_383[33]",33,"Reserved","Reserved"]
["WORD","READ",43291,"MTP01_N256_383[34]",34,"Reserved","Reserved"]
["WORD","READ",43292,"MTP01_N256_383[35]",35,"Reserved","Reserved"]
["WORD","READ",43293,"MTP01_N256_383[36]",36,"Reserved","Reserved"]
["WORD","READ",43294,"MTP01_N256_383[37]",37,"Reserved","Reserved"]
["WORD","READ",43295,"MTP01_N256_383[38]",38,"Reserved","Reserved"]
["WORD","READ",43296,"MTP01_N256_383[39]",39,"Reserved","Reserved"]
["WORD","READ",43297,"MTP01_N256_383[40]",40,"Reserved","Reserved"]
["WORD","READ",43298,"MTP01_N256_383[41]",41,"Reserved","Reserved"]
["WORD","READ",43299,"MTP01_N256_383[42]",42,"Reserved","Reserved"]
["WORD","READ",43300,"MTP01_N256_383[43]",43,"Reserved","Reserved"]
["WORD","READ",43301,"MTP01_N256_383[44]",44,"Reserved","Reserved"]
["WORD","READ",43302,"MTP01_N256_383[45]",45,"Reserved","Reserved"]
["WORD","READ",43303,"MTP01_N256_383[46]",46,"Reserved","Reserved"]
["WORD","READ",43304,"MTP01_N256_383[47]",47,"Reserved","Reserved"]
["WORD","READ",43305,"MTP01_N256_383[48]",48,"Reserved","Reserved"]
["WORD","READ",43306,"MTP01_N256_383[49]",49,"Reserved","Reserved"]
["WORD","READ",43307,"MTP01_N256_383[50]",50,"Reserved","Reserved"]
["WORD","READ",43308,"MTP01_N256_383[51]",51,"Reserved","Reserved"]
["WORD","READ",43309,"MTP01_N256_383[52]",52,"Reserved","Reserved"]
["WORD","READ",43310,"MTP01_N256_383[53]",53,"Reserved","Reserved"]
["WORD","READ",43311,"MTP01_N256_383[54]",54,"Reserved","Reserved"]
["WORD","READ",43312,"MTP01_N256_383[55]",55,"Reserved","Reserved"]
["WORD","READ",43313,"MTP01_N256_383[56]",56,"Reserved","Reserved"]
["WORD","READ",43314,"MTP01_N256_383[57]",57,"Reserved","Reserved"]
["WORD","READ",43315,"MTP01_N256_383[58]",58,"Reserved","Reserved"]
["WORD","READ",43316,"MTP01_N256_383[59]",59,"Reserved","Reserved"]
["WORD","READ",43317,"MTP01_N256_383[60]",60,"Reserved","Reserved"]
["WORD","READ",43318,"MTP01_N256_383[61]",61,"Reserved","Reserved"]
["WORD","READ",43319,"MTP01_N256_383[62]",62,"Reserved","Reserved"]
["WORD","READ",43320,"MTP01_N256_383[63]",63,"Reserved","Reserved"]
["WORD","READ",43321,"MTP01_N256_383[64]",64,"Reserved","Reserved"]
["WORD","READ",43322,{"$f":"CONCATENATE(\"MTP01_N256_383[\",E323,\"]\")","v":"MTP01_N256_383[65]"},65,"Reserved","Reserved"]
["WORD","READ",43323,"MTP01_N256_383[66]",66,"Reserved","Reserved"]
["WORD","READ",43324,"MTP01_N256_383[67]",67,"Reserved","Reserved"]
["WORD","READ",43325,"MTP01_N256_383[68]",68,"Reserved","Reserved"]
["WORD","READ",43326,"MTP01_N256_383[69]",69,"Reserved","Reserved"]
["WORD","READ",43327,"MTP01_N256_383[70]",70,"Reserved","Reserved"]
["WORD","READ",43328,"MTP01_N256_383[71]",71,"Reserved","Reserved"]
["WORD","READ",43329,"MTP01_N256_383[72]",72,"Reserved","Reserved"]
["WORD","READ",43330,"MTP01_N256_383[73]",73,"Reserved","Reserved"]
["WORD","READ",43331,"MTP01_N256_383[74]",74,"Reserved","Reserved"]
["WORD","READ",43332,"MTP01_N256_383[75]",75,"Reserved","Reserved"]
["WORD","READ",43333,"MTP01_N256_383[76]",76,"Reserved","Reserved"]
["WORD","READ",43334,"MTP01_N256_383[77]",77,"Reserved","Reserved"]
["WORD","READ",43335,"MTP01_N256_383[78]",78,"Reserved","Reserved"]
["WORD","READ",43336,"MTP01_N256_383[79]",79,"Reserved","Reserved"]
["WORD","READ",43337,"MTP01_N256_383[80]",80,"Reserved","Reserved"]
["WORD","READ",43338,"MTP01_N256_383[81]",81,"Reserved","Reserved"]
["WORD","READ",43339,"MTP01_N256_383[82]",82,"Reserved","Reserved"]
["WORD","READ",43340,"MTP01_N256_383[83]",83,"Reserved","Reserved"]
["WORD","READ",43341,"MTP01_N256_383[84]",84,"Reserved","Reserved"]
["WORD","READ",43342,"MTP01_N256_383[85]",85,"Reserved","Reserved"]
["WORD","READ",43343,"MTP01_N256_383[86]",86,"Reserved","Reserved"]
["WORD","READ",43344,"MTP01_N256_383[87]",87,"Reserved","Reserved"]
["WORD","READ",43345,"MTP01_N256_383[88]",88,"Reserved","Reserved"]
["WORD","READ",43346,"MTP01_N256_383[89]",89,"Reserved","Reserved"]
["WORD","READ",43347,"MTP01_N256_383[90]",90,"Reserved","Reserved"]
["WORD","READ",43348,"MTP01_N256_383[91]",91,"Reserved","Reserved"]
["WORD","READ",43349,"MTP01_N256_383[92]",92,"Reserved","Reserved"]
["WORD","READ",43350,"MTP01_N256_383[93]",93,"Reserved","Reserved"]
["WORD","READ",43351,"MTP01_N256_383[94]",94,"Reserved","Reserved"]
["WORD","READ",43352,"MTP01_N256_383[95]",95,"Reserved","Reserved"]
["WORD","READ",43353,"MTP01_N256_383[96]",96,"Reserved","Reserved"]
["WORD","READ",43354,"MTP01_N256_383[97]",97,"Reserved","Reserved"]
["WORD","READ",43355,"MTP01_N256_383[98]",98,"Reserved","Reserved"]
["WORD","READ",43356,"MTP01_N256_383[99]",99,"Reserved","Reserved"]
["WORD","READ",43357,"MTP01_N256_383[100]",100,"Reserved","Reserved"]
["WORD","READ",43358,"MTP01_N256_383[101]",101,"Reserved","Reserved"]
["WORD","READ",43359,"MTP01_N256_383[102]",102,"Reserved","Reserved"]
["WORD","READ",43360,"MTP01_N256_383[103]",103,"Reserved","Reserved"]
["WORD","READ",43361,"MTP01_N256_383[104]",104,"Reserved","Reserved"]
["WORD","READ",43362,"MTP01_N256_383[105]",105,"Reserved","Reserved"]
["WORD","READ",43363,"MTP01_N256_383[106]",106,"Reserved","Reserved"]
["WORD","READ",43364,"MTP01_N256_383[107]",107,"Reserved","Reserved"]
["WORD","READ",43365,"MTP01_N256_383[108]",108,"Reserved","Reserved"]
["WORD","READ",43366,"MTP01_N256_383[109]",109,"Reserved","Reserved"]
["WORD","READ",43367,"MTP01_N256_383[110]",110,"Reserved","Reserved"]
["WORD","READ",43368,"MTP01_N256_383[111]",111,"Reserved","Reserved"]
["WORD","READ",43369,"MTP01_N256_383[112]",112,"Reserved","Reserved"]
["WORD","READ",43370,"MTP01_N256_383[113]",113,"Reserved","Reserved"]
["WORD","READ",43371,"MTP01_N256_383[114]",114,"Reserved","Reserved"]
["WORD","READ",43372,"MTP01_N256_383[115]",115,"Reserved","Reserved"]
["WORD","READ",43373,"MTP01_N256_383[116]",116,"Reserved","Reserved"]
["WORD","READ",43374,"MTP01_N256_383[117]",117,"Reserved","Reserved"]
["WORD","READ",43375,"MTP01_N256_383[118]",118,"Reserved","Reserved"]
["WORD","READ",43376,"MTP01_N256_383[119]",119,"Reserved","Reserved"]
["WORD","READ",43377,"MTP01_N256_383[120]",120,"Reserved","Reserved"]
["WORD","READ",43378,"MTP01_N256_383[121]",121,"Reserved","Reserved"]
["WORD","READ",43379,"MTP01_N256_383[122]",122,"Reserved","Reserved"]
["WORD","READ",43380,"MTP01_N256_383[123]",123,"Reserved","Reserved"]
["WORD","READ",43381,"MTP01_N256_383[124]",124,"Reserved","Reserved"]
["WORD","READ",43382,"MTP01_N256_383[125]",125,"Reserved","Reserved"]
["WORD","READ",43383,"MTP01_N256_383[126]",126,"Reserved","Reserved"]
["WORD","READ",43384,"MTP01_N256_383[127]",127,"Reserved","Reserved"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["ADDRESS TYPE","READ/WRITE","RELATIVE MODBUS","RELATIVE COMPACT LOGIX ADDRESS",null,"DESCRIPTION","DATA"]
["BOOLEAN","WRITE",513,{"$f":"CONCATENATE(\"MTP1_B01[\",E401,\"]\")","v":"MTP1_B01[0]"},0,"_RMT_COMP_START"]
["BOOLEAN","WRITE",514,{"$f":"CONCATENATE(\"MTP1_B01[\",E402,\"]\")","v":"MTP1_B01[1]"},1,"_RMT_COMP_IMMEDIATE_STOP"]
["BOOLEAN","WRITE",515,"MTP1_B01[2]",2,"_RMT_COMP_FULL_LOAD"]
["BOOLEAN","WRITE",516,"MTP1_B01[3]",3,"_RMT_COMP_LOAD_LIMIT"]
["BOOLEAN","WRITE",517,"MTP1_B01[4]",4,"RESERVED"]
["BOOLEAN","WRITE",518,"MTP1_B01[5]",5,"_RMT_CHILL_LBT_100PERCENT"]
["BOOLEAN","WRITE",519,"MTP1_B01[6]",6,"RESERVED"]
["BOOLEAN","WRITE",520,"MTP1_B01[7]",7,"RESERVED"]
["BOOLEAN","WRITE",521,"MTP1_B01[8]",8,"RESERVED"]
["BOOLEAN","WRITE",522,"MTP1_B01[9]",9,"RESERVED"]
["BOOLEAN","WRITE",523,"MTP1_B01[10]",10,"RESERVED"]
["BOOLEAN","WRITE",524,"MTP1_B01[11]",11,"RESERVED"]
["BOOLEAN","WRITE",525,"MTP1_B01[12]",12,"RESERVED"]
["BOOLEAN","WRITE",526,"MTP1_B01[13]",13,"RESERVED"]
["BOOLEAN","WRITE",527,"MTP1_B01[14]",14,"RESERVED"]
["BOOLEAN","WRITE",528,"MTP1_B01[15]",15,"RESERVED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[16]",16,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[17]",17,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[18]",18,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[19]",19,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[20]",20,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[21]",21,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[22]",22,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[23]",23,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[24]",24,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[25]",25,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[26]",26,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[27]",27,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[28]",28,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[29]",29,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[30]",30,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B01[31]",31,"NOT USED"]
["ADDRESS TYPE","READ/WRITE","RELATIVE MODBUS","RELATIVE COMPACT LOGIX ADDRESS",null,"DESCRIPTION","DATA"]
["BOOLEAN","WRITE",561,{"$f":"CONCATENATE(\"MTP1_B02[\",E434,\"]\")","v":"MTP1_B02[0]"},0,"RESERVED"]
["BOOLEAN","WRITE",562,{"$f":"CONCATENATE(\"MTP1_B02[\",E435,\"]\")","v":"MTP1_B02[1]"},1,"RESERVED"]
["BOOLEAN","WRITE",563,"MTP1_B02[2]",2,"RESERVED"]
["BOOLEAN","WRITE",564,"MTP1_B02[3]",3,"RESERVED"]
["BOOLEAN","WRITE",565,"MTP1_B02[4]",4,"RESERVED"]
["BOOLEAN","WRITE",566,"MTP1_B02[5]",5,"RESERVED"]
["BOOLEAN","WRITE",567,"MTP1_B02[6]",6,"RESERVED"]
["BOOLEAN","WRITE",568,"MTP1_B02[7]",7,"RESERVED"]
["BOOLEAN","WRITE",569,"MTP1_B02[8]",8,"RESERVED"]
["BOOLEAN","WRITE",570,"MTP1_B02[9]",9,"RESERVED"]
["BOOLEAN","WRITE",571,"MTP1_B02[10]",10,"RESERVED"]
["BOOLEAN","WRITE",572,"MTP1_B02[11]",11,"RESERVED"]
["BOOLEAN","WRITE",573,"MTP1_B02[12]",12,"RESERVED"]
["BOOLEAN","WRITE",574,"MTP1_B02[13]",13,"RESERVED"]
["BOOLEAN","WRITE",575,"MTP1_B02[14]",14,"RESERVED"]
["BOOLEAN","WRITE",576,"MTP1_B02[15]",15,"COMMUNICATION CLEAR ALARM"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[16]",16,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[17]",17,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[18]",18,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[19]",19,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[20]",20,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[21]",21,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[22]",22,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[23]",23,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[24]",24,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[25]",25,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[26]",26,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[27]",27,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[28]",28,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[29]",29,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[30]",30,"NOT USED"]
["BOOLEAN","NOT USED","NOT USED","MTP1_B02[31]",31,"NOT USED"]

{"sheet":"LOW16 & HIGH 16 BITS","index":1,"n_rows":59,"n_cols":6,"rows_kept":59,"cut":false,"hidden":false,"merged":[[45,0,46,0],[47,0,49,0],[50,0,53,0],[54,0,56,0],[34,0,35,0],[37,0,38,0],[39,0,40,0],[41,0,42,0],[43,0,44,0],[23,0,24,0],[26,0,27,0],[28,0,29,0],[30,0,31,0],[32,0,33,0],[5,0,6,0],[7,0,8,0],[9,0,11,0],[12,0,13,0],[14,0,17,0],[12,2,13,2],[12,1,13,1],[26,2,27,2],[9,2,11,2],[5,2,6,2],[5,1,6,1],[7,1,8,1],[7,2,8,2],[26,1,27,1],[14,2,17,2],[14,1,17,1],[23,1,24,1],[23,2,24,2],[9,1,11,1],[30,5,31,5],[30,3,31,3],[26,5,27,5],[12,5,13,5],[14,5,17,5],[26,3,27,3],[12,3,13,3],[14,3,17,3],[23,3,24,3],[23,5,24,5],[28,3,29,3],[28,5,29,5],[5,5,6,5],[7,5,8,5],[9,5,11,5],[9,3,11,3],[7,3,8,3],[5,3,6,3],[32,5,33,5],[32,3,33,3],[34,3,35,3],[34,2,35,2],[32,2,33,2],[34,5,35,5],[32,1,33,1],[28,1,29,1],[28,2,29,2],[34,1,35,1],[30,2,31,2],[30,1,31,1],[39,5,40,5],[39,3,40,3],[39,2,40,2],[39,1,40,1],[37,1,38,1],[37,2,38,2],[37,3,38,3],[37,5,38,5],[43,5,44,5],[45,5,46,5],[41,1,42,1],[41,2,42,2],[41,3,42,3],[41,5,42,5],[45,3,46,3],[43,3,44,3],[43,2,44,2],[43,1,44,1],[45,1,46,1],[45,2,46,2],[54,5,56,5],[54,3,56,3],[50,3,53,3],[47,1,49,1],[47,5,49,5],[47,3,49,3],[47,2,49,2],[50,5,53,5],[54,2,56,2],[54,1,56,1],[50,1,53,1],[50,2,53,2]]}
["ADDRESS","CoilNumber","Attribute","Internal Bit Device","Name","Category"]
[43001,1,"Read Only","Y0000h","Compressor Start","Real DI/O"]
[43001.1,2,"Read Only","Y0001h","Oil Pump Start","Real DI/O"]
[43001.2,3,"Read Only","Y0002h","Low Stage Load SV","Real DI/O"]
[43001.3,4,"Read Only","Y0003h","Low Stage Unload SV","Real DI/O"]
[43001.4,5,"Read Only","Y0004h","Liquid Injection Supply SV","Real DI/O"]
[null,null,null,null,"High Stage Load SV"]
[43001.5,6,"Read Only","Y0005h","Liquid Injection YOSAKU SV","Real DI/O"]
[null,null,null,null,"High Stage Unload SV"]
[43001.599999999999,7,"Read Only","Y0006h","Oil Heater","Real DI/O"]
[null,null,null,null,"Chiller Supply SV1of3(!NORTH AMERICA)"]
[null,null,null,null,"J Economizer/Intercooler supply SV"]
[43001.7,8,"Read Only","Y0007h","Economizer/Intercooler Supply SV","Real DI/O"]
[null,null,null,null,"J Vi Increase SV"]
[43001.8,9,"Read Only","Y0008h","Oil Feed SV","Real DI/O"]
[null,null,null,null,"Oil Drain SV"]
[null,null,null,null,"J Vi Decrease SV"]
[null,null,null,null,"FM160 Oil Return SV"]
[43001.9,10,"Read Only","Y0009h","Alarm/Failure","Real DI/O"]
[43001.1,11,"Read Only","X000Ah","Emergency Stop Input","Real DI/O"]
[43001.11,12,"Read Only","X000Bh","Compressor Motor Starter Read Back","Real DI/O"]
[43001.120000000003,13,"Read Only","X000Ch","Interlock-1","Real DI/O"]
[43001.13,14,"Read Only","X000Dh","Interlock-2(Cooling Water Flow SW)","Real DI/O"]
[43001.14,15,"Read Only","X000Eh","Interlock-3(Process Flow SW)","Real DI/O"]
[null,null,null,null,"J or FM160 Oil Level SW"]
[43001.15,16,"Read Only","X000Fh","Remote Start/Stop Input","Real DI/O"]
[43002,17,"Read Only","Y0010h","Chiller Supply SV1of3","Real DI/O"]
[null,null,null,null,"UD-V M Drain SV"]
[43002.1,18,"Read Only","Y0011h","Chiller YOSAKU SV1of3","Real DI/O"]
[null,null,null,null,"UD-V M Plug SV"]
[43002.2,19,"Read Only","Y0012h","Chiller Pump Start","Real DI/O"]
[null,null,null,null,"UD-V Bypass SV"]
[43002.3,20,"Read Only","Y0013h","Starting Bypass SV","Real DI/O"]
[null,null,null,null,"Hot Gas Bypass SV"]
[43002.400000000001,21,"Read Only","Y0014h","Economizer/Intercooler YOSAKU SV","Real DI/O"]
[null,null,null,null,"Oil Pump #2 Start"]
[43002.5,22,"Read Only","Y0015h","Alarm","Real DI/O"]
[43002.6,23,"Read Only","Y0016h","Chiller Supply SV2of3","Real DI/O"]
[null,null,null,null,"UD-V LH Increase SV"]
[43002.7,24,"Read Only","Y0017h","Chiller YOSAKU SV2of3","Real DI/O"]
[null,null,null,null,"UD-V LH Decrease SV"]
[43002.8,25,"Read Only","Y0018h","Condenser Out1of6","Real DI/O"]
[null,null,null,null,"Auxiliary Start"]
[43002.9,26,"Read Only","Y0019h","Condenser Out2of6","Real DI/O"]
[null,null,null,null,"UD-V M Drain SV"]
[43002.1,27,"Read Only","Y001Ah","Condenser Out3of6","Real DI/O"]
[null,null,null,null,"UD-V M Plug SV"]
[43002.11,28,"Read Only","Y001Bh","Condenser Out4of6","Real DI/O"]
[null,null,null,null,"UD-V Bypass SV"]
[null,null,null,null,"Liquid Injection YOSAKU SV #2"]
[43002.12,29,"Read Only","Y001Ch","Condenser Out5of6","Real DI/O"]
[null,null,null,null,"UD-V LH Increase SV"]
[null,null,null,null,"Ready to Start Bit"]
[null,null,null,null,"Chiller Supply SV3of 3"]
[43002.13,30,"Read Only","Y001Dh","Condenser Out6of6","Real DI/O"]
[null,null,null,null,"UD-V LH Decrease SV"]
[null,null,null,null,"Chiller YOSAKU SV3of 3"]
[43002.14,31,"Read Only","X001Eh","Remote Load Input","Real DI/O"]
[43002.15,32,"Read Only","X001Fh","Remote Unload Input","Real DI/O"]

{"sheet":"Alarm & Failure Bit Sheet","index":2,"n_rows":137,"n_cols":5,"rows_kept":137,"cut":false,"hidden":false,"merged":[[49,0,64,0],[49,1,64,1],[49,2,64,2],[49,4,64,4],[17,0,32,0],[17,1,32,1],[17,2,32,2],[17,4,32,4],[33,0,48,0],[33,1,48,1],[33,2,48,2],[33,4,48,4],[0,0,0,2],[1,0,16,0],[1,1,16,1],[1,2,16,2],[1,4,16,4]]}
["Holding Register",null,null,"Bit Alignment","Reference"]
["Read Only",43003,"ALARM No.  1 to  16","Bit 0:Undefined",40281]
[null,null,null,"Bit 1:⊿OP LOW"]
[null,null,null,"Bit 2:⊿P LOW"]
[null,null,null,"Bit 3:DISCHARGE PRESSURE HIGH"]
[null,null,null,"Bit 4:DISCHARGE TEMPERATURE HIGH"]
[null,null,null,"Bit 5:OIL SUPPLY TEMPERATURE HIGH"]
[null,null,null,"Bit 6:COMPRESSOR MOTOR CURRENT HIGH"]
[null,null,null,"Bit 7:INTERMEDIATE PRESSURE HIGH"]
[null,null,null,"Bit 8:SUCTION PRESSURE LOW"]
[null,null,null,"Bit 9:LEAVING BRINE TEMPERATURE LOW"]
[null,null,null,"Bit10:CAPACITY NO DOWN"]
[null,null,null,"Bit11:SUCTION SUPERHEAT LOW"]
[null,null,null,"Bit12:OIL FILTER"]
[null,null,null,"Bit13:RE-START"]
[null,null,null,"Bit14:HIGH STAGE"]
[null,null,null,"Bit15:INTERMEDIATE SUPERHEAT LOW"]
["Read Only",43004,"ALARM No. 17 to  32","Bit 0:ENTERING BRINE TEMPERATURE LOW",40282]
[null,null,null,"Bit 1:SEPARATOR OIL TEMPERATURE LOW"]
[null,null,null,"Bit 2:⊿OP2 LOW"]
[null,null,null,"Bit 3:SUCTION SUPERHEAT2 LOW"]
[null,null,null,"Bit 4:AUTO Vi SLIDE"]
[null,null,null,"Bit 5:FINE FILTER"]
[null,null,null,"Bit 6:DISCHARGE SUPERHEAT LOW"]
[null,null,null,"Bit 7:SUCTION PRESSURE HIGH"]
[null,null,null,"Bit 8:SUCTION TEMPERATURE HIGH"]
[null,null,null,"Bit 9:CHILLER LIQUID LEVEL LOW"]
[null,null,null,"Bit10:Undefined"]
[null,null,null,"Bit11:Undefined"]
[null,null,null,"Bit12:Undefined"]
[null,null,null,"Bit13:Undefined"]
[null,null,null,"Bit14:Undefined"]
[null,null,null,"Bit15:Undefined"]
["Read Only",43005,"ALARM No. 33 to 48","Bit 0:AUTO STAGE NO REQUEST",40283]
[null,null,null,"Bit 1:AUTO STAGE LIST1 NO RESPONSE"]
[null,null,null,"Bit 2:AUTO STAGE LIST2 NO RESPONSE"]
[null,null,null,"Bit 3:AUTO STAGE LIST3 NO RESPONSE"]
[null,null,null,"Bit 4:AUTO STAGE LIST4 NO RESPONSE"]
[null,null,null,"Bit 5:AUTO STAGE LIST5 NO RESPONSE"]
[null,null,null,"Bit 6:AUTO STAGE LIST6 NO RESPONSE"]
[null,null,null,"Bit 7:AUTO STAGE LIST7 NO RESPONSE"]
[null,null,null,"Bit 8:AUTO STAGE LIST8 NO RESPONSE"]
[null,null,null,"Bit 9:OPTION ANALOG INPUT1 LOW"]
[null,null,null,"Bit10:OPTION ANALOG INPUT1 HIGH"]
[null,null,null,"Bit11:OPTION ANALOG INPUT2 LOW"]
[null,null,null,"Bit12:OPTION ANALOG INPUT2 HIGH"]
[null,null,null,"Bit13:OPTION ANALOG INPUT3 LOW"]
[null,null,null,"Bit14:OPTION ANALOG INPUT3 HIGH"]
[null,null,null,"Bit15:OPTION ANALOG INPUT4 LOW"]
["Read Only",43006,"ALARM No. 49 to  64","Bit 0:OPTION ANALOG INPUT4 HIGH",40284]
[null,null,null,"Bit 1:Undefined (Always OFF.)"]
[null,null,null,"Bit 2:Undefined (Always OFF.)"]
[null,null,null,"Bit 3:Undefined (Always OFF.)"]
[null,null,null,"Bit 4:Undefined (Always OFF.)"]
[null,null,null,"Bit 5:Undefined (Always OFF.)"]
[null,null,null,"Bit 6:Undefined (Always OFF.)"]
[null,null,null,"Bit 7:Undefined (Always OFF.)"]
[null,null,null,"Bit 8:Undefined (Always OFF.)"]
[null,null,null,"Bit 9:Undefined (Always OFF.)"]
[null,null,null,"Bit10:Undefined (Always OFF.)"]
[null,null,null,"Bit11:Undefined (Always OFF.)"]
[null,null,null,"Bit12:Undefined (Always OFF.)"]
[null,null,null,"Bit13:Undefined (Always OFF.)"]
[null,null,null,"Bit14:Undefined (Always OFF.)"]
[null,null,null,"Bit15:Undefined (Always OFF.)"]
["Read Only",43007,"ALARM No. 65 to  80","Undefined (Always Zero.)",40285]
["Read Only",43008,"ALARM No. 80 to  96","Undefined (Always Zero.)",40286]
["Read Only",43009,"ALARM No. 97 to 112","Undefined (Always Zero.)",40287]
["Read Only",43010,"ALARM No.113 to 128","Undefined (Always Zero.)",40288]
["Read Only",43011,"FAILURE No.  1 to  16","Bit 0:START",40289]
[null,null,null,"Bit 1:⊿OP LOW"]
[null,null,null,"Bit 2:⊿P LOW"]
[null,null,null,"Bit 3:DISCHARGE PRESSURE HIGH"]
[null,null,null,"Bit 4:DISCHARGE TEMPERATURE HIGH"]
[null,null,null,"Bit 5:OIL SUPPLY TEMPERATURE HIGH"]
[null,null,null,"Bit 6:COMPRESSOR MOTOR CURRENT HIGH"]
[null,null,null,"Bit 7:OIL FILTER"]
[null,null,null,"Bit 8:INTERLOCK-2"]
[null,null,null,"Bit 9:EMERGENCY STOP"]
[null,null,null,"Bit10:OIL LEVEL LOW"]
[null,null,null,"Bit11:FINE FILTER"]
[null,null,null,"Bit12:INTERMEDIATE PRESSURE HIGH"]
[null,null,null,"Bit13:INTERLOCK"]
[null,null,null,"Bit14:LEAVING BRINE TEMPERATURE LOW"]
[null,null,null,"Bit15:INTERLOCK-3"]
["Read Only",43012,"FAILURE No. 17 to  32","Bit 0:SUCTION PRESSURE LOW",40290]
[null,null,null,"Bit 1:SUCTION PRESSURE OVER RANGE"]
[null,null,null,"Bit 2:DISCHARGE PRESSURE UNDER RANGE"]
[null,null,null,"Bit 3:OIL SUPPLY PRESSURE OVER RANGE"]
[null,null,null,"Bit 4:OIL FILTER PRESSURE OVER RANGE"]
[null,null,null,"Bit 5:SUCTION TEMPERATURE UNDER/OVER RANGE"]
[null,null,null,"Bit 6:DISCHARGE TEMPERATURE UNDER RANGE"]
[null,null,null,"Bit 7:OIL SUPPLY TEMPERATURE UNDER RANGE"]
[null,null,null,"Bit 8:INTERMEDIATE PRESSURE UNDER RANGE"]
[null,null,null,"Bit 9:INTERMEDIATE TEMPERATURE UNDER/OVER RANGE"]
[null,null,null,"Bit10:COMPRESSOR MOTOR CURRENT UNDER RANGE"]
[null,null,null,"Bit11:LEAVING BRINE TEMPERATURE OVER RANGE"]
[null,null,null,"Bit12:LOW SLIDE VALVE POSITION UNDER/OVER RANGE"]
[null,null,null,"Bit13:HIGH SLIDE VALVE POSITION UNDER/OVER RANGE"]
[null,null,null,"Bit14:CHILLER GAS TEMPERATURE1&2 UNDER/OVER RANGE"]
[null,null,null,"Bit15:SUCTION PRESSURE1&2 UNDER/OVER RANGE"]
["Read Only",43013,"FAILURE No. 33 to  48","Bit 0:Undefined (Always OFF.)",40291]
[null,null,null,"Bit 1:SUCTION SUPERHEAT LOW"]
[null,null,null,"Bit 2:SUCTION SUPERHEAT2 LOW"]
[null,null,null,"Bit 3:SUCTION PRESSURE HIGH"]
[null,null,null,"Bit 4:SUCTION TEMPERATURE HIGH"]
[null,null,null,"Bit 5:Undefined (Always OFF.)"]
[null,null,null,"Bit 6:Undefined (Always OFF.)"]
[null,null,null,"Bit 7:Undefined (Always OFF.)"]
[null,null,null,"Bit 8:Undefined (Always OFF.)"]
[null,null,null,"Bit 9:OPTION ANALOG INPUT1 LOW"]
[null,null,null,"Bit10:OPTION ANALOG INPUT1 HIGH"]
[null,null,null,"Bit11:OPTION ANALOG INPUT2 LOW"]
[null,null,null,"Bit12:OPTION ANALOG INPUT2 HIGH"]
[null,null,null,"Bit13:OPTION ANALOG INPUT3 LOW"]
[null,null,null,"Bit14:OPTION ANALOG INPUT3 HIGH"]
[null,null,null,"Bit15:OPTION ANALOG INPUT4 LOW"]
["Read Only",43014,"FAILURE No. 49 to  64","Bit 0:OPTION ANALOG INPUT4 HIGH",40292]
[null,null,null,"Bit 1:Undefined (Always OFF.)"]
[null,null,null,"Bit 2:Undefined (Always OFF.)"]
[null,null,null,"Bit 3:Undefined (Always OFF.)"]
[null,null,null,"Bit 4:Undefined (Always OFF.)"]
[null,null,null,"Bit 5:Undefined (Always OFF.)"]
[null,null,null,"Bit 6:Undefined (Always OFF.)"]
[null,null,null,"Bit 7:Undefined (Always OFF.)"]
[null,null,null,"Bit 8:Undefined (Always OFF.)"]
[null,null,null,"Bit 9:Undefined (Always OFF.)"]
[null,null,null,"Bit10:Undefined (Always OFF.)"]
[null,null,null,"Bit11:Undefined (Always OFF.)"]
[null,null,null,"Bit12:Undefined (Always OFF.)"]
[null,null,null,"Bit13:Undefined (Always OFF.)"]
[null,null,null,"Bit14:Undefined (Always OFF.)"]
[null,null,null,"Bit15:Undefined (Always OFF.)"]
["Read Only",43015,"FAILURE No. 65 to  80","Undefined (Always Zero.)",40293]
["Read Only",43016,"FAILURE No. 80 to  96","Undefined (Always Zero.)",40294]
["Read Only",43017,"FAILURE No. 97 to 112","Undefined (Always Zero.)",40295]
["Read Only",43018,"FAILURE No.113 to 128","Undefined (Always Zero.)",40296]